## Wu2009
Paper information
Authors | Wu et al.
Title | Numerical investigation on the heat and mass transfer in a direct evaporative cooler
Year | 2009
Data type | Exerimental, from table and numerical, from graphs
Description | Study of a crossflow DEC with matrix made of a GLASdek pad material with a cross-fluted, unequal angle pad design to induce turbulent mixing of air and water for optimum heat and moisture transfer. 1. Comparison of simulation results with experimental data. 2. Study of the impact of inlet temperature and humidity, air velocity, and pad length on the DEC efficiency.
HEX characteristics |  |  | Configuration
HEX type | DEC |  | pd | wf
Water injection type | Wet surface |  | Crossflow
Water recirculation | Yes
Wall material | GLASdek
Configuration | XF
Geometry
Length | 0.138 | m
Width | 0.3 | m
Height | NA | m
Channel height | 0.006 | m
Wall thickness | NA | m
Number of channels | NA | -
Operating conditions
Primary fluid velocity | 1-4 | m/s
Water supplied | NA | kg/s
| Testing conditions | [7 empty] | Inlet conditions |  |  |  |  | Outlet conditions
Run | Test | L | h_ch | W | WWR | Re | Nu | h_T | T_pwi | w_pwi | v_pwi | T_wfi | m_dot_wf | T_pwo | w_pwo | epsilon_wb
1 | E | 0.138 | 0.006 | 0.3 | 1 | 1520.1413 | 7.54 | 16.482 | 27.21 | 0.011939 | 2 | NA | NA | 22.9 | 0.01364 | 0.61048
2 | E | 0.138 | 0.006 | 0.3 | 1 | 1521.2125 | 7.54 | 16.4927 | 27.84 | 0.010235 | 2 | NA | NA | 22.66 | 0.012286 | 0.58998
3 | E | 0.138 | 0.006 | 0.3 | 1 | 1511.4838 | 7.54 | 16.5262 | 28.54 | 0.011929 | 2 | NA | NA | 23.5 | 0.013934 | 0.63079
4 | E | 0.138 | 0.006 | 0.3 | 1 | 1508.5121 | 7.54 | 16.5416 | 28.9 | 0.011917 | 2 | NA | NA | 23.81 | 0.013954 | 0.61697
5 | E | 0.138 | 0.006 | 0.3 | 1 | 1517.7582 | 7.54 | 16.5213 | 29.32 | 0.0090837 | 2 | NA | NA | 22.37 | 0.011893 | 0.65075
6 | E | 0.138 | 0.006 | 0.3 | 1 | 1506.089 | 7.54 | 16.5654 | 29.91 | 0.010733 | 2 | NA | NA | 23.78 | 0.013168 | 0.62424
7 | E | 0.138 | 0.006 | 0.3 | 1 | 1511.0146 | 7.54 | 16.5579 | 30.5 | 0.0088761 | 2 | NA | NA | 22.77 | 0.012005 | 0.66409
8 | E | 0.138 | 0.006 | 0.3 | 1 | 1501.9113 | 7.54 | 16.5948 | 30.83 | 0.0099239 | 2 | NA | NA | 24.1 | 0.012606 | 0.6085
9 | E | 0.138 | 0.006 | 0.3 | 1 | 1472.5586 | 7.54 | 16.6809 | 31.5 | 0.016894 | 2 | NA | NA | 27.6 | 0.018483 | 0.57269
10 | E | 0.138 | 0.006 | 0.3 | 1 | 1486.3768 | 7.54 | 16.6464 | 31.86 | 0.012959 | 2 | NA | NA | 25.49 | 0.015572 | 0.66285
11 | E | 0.138 | 0.006 | 0.3 | 1 | 1498.1898 | 7.54 | 16.6267 | 32.31 | 0.0086305 | 2 | NA | NA | 23.94 | 0.011957 | 0.64089
12 | E | 0.138 | 0.006 | 0.3 | 1 | 1497.588 | 7.54 | 16.6426 | 32.86 | 0.0073227 | 2 | NA | NA | 24.01 | 0.010842 | 0.61203
13 | E | 0.138 | 0.006 | 0.3 | 1 | 1483.1552 | 7.54 | 16.6762 | 33.09 | 0.011632 | 2 | NA | NA | 25.49 | 0.014661 | 0.66667
14 | E | 0.138 | 0.006 | 0.3 | 1 | 1470.6255 | 7.54 | 16.725 | 33.73 | 0.013417 | 2 | NA | NA | 27.1 | 0.016076 | 0.62254
15 | E | 0.138 | 0.006 | 0.3 | 1 | 1481.2369 | 7.54 | 16.7067 | 34.06 | 0.0095537 | 2 | NA | NA | 25.73 | 0.012943 | 0.61385
16 | E | 0.138 | 0.006 | 0.3 | 1 | 1466.8281 | 7.54 | 16.7465 | 34.46 | 0.013279 | 2 | NA | NA | 27.31 | 0.016185 | 0.63443
17 | E | 0.138 | 0.006 | 0.3 | 1 | 1477.3081 | 7.54 | 16.7331 | 35.01 | 0.0089848 | 2 | NA | NA | 25.9 | 0.012652 | 0.62184
18 | E | 0.138 | 0.006 | 0.3 | 1 | 1458.4093 | 7.54 | 16.7888 | 35.81 | 0.013563 | 2 | NA | NA | 27.84 | 0.016817 | 0.66031
19 | E | 0.138 | 0.006 | 0.3 | 1 | 1437.3383 | 7.54 | 16.8626 | 36.8 | 0.017631 | 2 | NA | NA | 30.4 | 0.020196 | 0.61836
20 | E | 0.138 | 0.006 | 0.3 | 1 | 1454.0097 | 7.54 | 16.8226 | 37.06 | 0.012545 | 2 | NA | NA | 28.01 | 0.016145 | 0.66349
21 | N | 0.138 | 0.006 | 0.3 | 1 | 729.6657 | 7.54 | 16.7599 | 35 | 0.016 | 1 | NA | NA | 27.5342 | 0.019028 | 0.74981
22 | N | 0.138 | 0.006 | 0.3 | 1 | 1092.513 | 7.54 | 16.7741 | 35 | 0.016 | 1.5 | NA | NA | 28.1614 | 0.018772 | 0.68707
23 | N | 0.138 | 0.006 | 0.3 | 1 | 1454.1698 | 7.54 | 16.7876 | 35 | 0.016 | 2 | NA | NA | 28.7586 | 0.018527 | 0.62662
24 | N | 0.138 | 0.006 | 0.3 | 1 | 1815.0478 | 7.54 | 16.799 | 35 | 0.016 | 2.5 | NA | NA | 29.2663 | 0.01832 | 0.57643
25 | N | 0.138 | 0.006 | 0.3 | 1 | 2176.1801 | 7.54 | 16.8058 | 35 | 0.016 | 3 | NA | NA | 29.5649 | 0.018202 | 0.54563
26 | N | 0.138 | 0.006 | 0.3 | 1 | 2537.2727 | 8.2473 | 18.3877 | 35 | 0.016 | 3.5 | NA | NA | 29.7839 | 0.018113 | 0.52395
27 | N | 0.138 | 0.006 | 0.3 | 1 | 2897.576 | 9.6722 | 21.5721 | 35 | 0.016 | 4 | NA | NA | 30.0427 | 0.018007 | 0.49772
28 | N | 0.2 | 0.006 | 0.3 | 1 | 732.7696 | 7.54 | 16.7268 | 35 | 0.016 | 1 | NA | NA | 26.0709 | 0.019624 | 0.89696
29 | N | 0.2 | 0.006 | 0.3 | 1 | 1097.7258 | 7.54 | 16.7369 | 35 | 0.016 | 1.5 | NA | NA | 26.5189 | 0.01944 | 0.85247
30 | N | 0.2 | 0.006 | 0.3 | 1 | 1461.7335 | 7.54 | 16.747 | 35 | 0.016 | 2 | NA | NA | 26.9668 | 0.019256 | 0.80684
31 | N | 0.2 | 0.006 | 0.3 | 1 | 1825.2696 | 7.54 | 16.7552 | 35 | 0.016 | 2.5 | NA | NA | 27.3252 | 0.01911 | 0.77148
32 | N | 0.2 | 0.006 | 0.3 | 1 | 2187.7352 | 7.54 | 16.7644 | 35 | 0.016 | 3 | NA | NA | 27.7333 | 0.018947 | 0.73042
33 | N | 0.2 | 0.006 | 0.3 | 1 | 2550.1518 | 8.3004 | 18.4624 | 35 | 0.016 | 3.5 | NA | NA | 28.032 | 0.018824 | 0.69962
34 | N | 0.2 | 0.006 | 0.3 | 1 | 2912.7805 | 9.7309 | 21.6501 | 35 | 0.016 | 4 | NA | NA | 28.231 | 0.018743 | 0.68023
35 | N | 0.138 | 0.006 | 0.3 | 1 | 1506.207 | 7.54 | 16.5663 | 30 | 0.010575 | 2 | NA | NA | 23.7218 | 0.013128 | 0.6292
36 | N | 0.138 | 0.006 | 0.3 | 1 | 1501.1145 | 7.54 | 16.5967 | 31 | 0.01016 | 2 | NA | NA | 24.0231 | 0.013008 | 0.63628
37 | N | 0.138 | 0.006 | 0.3 | 1 | 1495.5821 | 7.54 | 16.6295 | 32 | 0.0097454 | 2 | NA | NA | 24.4306 | 0.012741 | 0.6292
38 | N | 0.138 | 0.006 | 0.3 | 1 | 1490.2708 | 7.54 | 16.6613 | 33 | 0.0093316 | 2 | NA | NA | 24.7951 | 0.012591 | 0.63009
39 | N | 0.138 | 0.006 | 0.3 | 1 | 1484.7557 | 7.54 | 16.6943 | 34 | 0.0089185 | 2 | NA | NA | 25.2133 | 0.012425 | 0.62655
40 | N | 0.138 | 0.006 | 0.3 | 1 | 1479.5729 | 7.54 | 16.7258 | 35 | 0.0085059 | 2 | NA | NA | 25.5622 | 0.012282 | 0.6292
41 | N | 0.138 | 0.006 | 0.3 | 1 | 1474.3685 | 7.54 | 16.7576 | 36 | 0.008094 | 2 | NA | NA | 25.9228 | 0.012134 | 0.63009
42 | N | 0.138 | 0.006 | 0.3 | 1 | 1496.2951 | 7.54 | 16.5907 | 30 | 0.013371 | 2 | NA | NA | 24.9325 | 0.01545 | 0.63451
43 | N | 0.138 | 0.006 | 0.3 | 1 | 1490.7489 | 7.54 | 16.6236 | 31 | 0.012953 | 2 | NA | NA | 25.3505 | 0.015282 | 0.63009
44 | N | 0.138 | 0.006 | 0.3 | 1 | 1485.555 | 7.54 | 16.6548 | 32 | 0.012535 | 2 | NA | NA | 25.695 | 0.015041 | 0.6292
45 | N | 0.138 | 0.006 | 0.3 | 1 | 1480.2908 | 7.54 | 16.6865 | 33 | 0.012117 | 2 | NA | NA | 26.0625 | 0.014897 | 0.63009
46 | N | 0.138 | 0.006 | 0.3 | 1 | 1474.8596 | 7.54 | 16.7193 | 34 | 0.0117 | 2 | NA | NA | 26.4758 | 0.014728 | 0.62655
47 | N | 0.138 | 0.006 | 0.3 | 1 | 1469.9913 | 7.54 | 16.7493 | 35 | 0.011284 | 2 | NA | NA | 26.7648 | 0.014615 | 0.63363
48 | N | 0.138 | 0.006 | 0.3 | 1 | 1464.4955 | 7.54 | 16.7829 | 36 | 0.010869 | 2 | NA | NA | 27.2075 | 0.014432 | 0.6292
49 | N | 0.1 | 0.006 | 0.3 | 1 | 1447.2919 | 7.54 | 16.8247 | 35 | 0.016 | 2 | NA | NA | 30.4011 | 0.017861 | 0.46196
50 | N | 0.125 | 0.006 | 0.3 | 1 | 1452.1635 | 7.54 | 16.7984 | 35 | 0.016 | 2 | NA | NA | 29.2364 | 0.018332 | 0.57909
51 | N | 0.15 | 0.006 | 0.3 | 1 | 1456.0547 | 7.54 | 16.7774 | 35 | 0.016 | 2 | NA | NA | 28.3107 | 0.01871 | 0.67229
52 | N | 0.175 | 0.006 | 0.3 | 1 | 1459.2473 | 7.54 | 16.7603 | 35 | 0.016 | 2 | NA | NA | 27.5541 | 0.01902 | 0.74786
53 | N | 0.2 | 0.006 | 0.3 | 1 | 1461.9867 | 7.54 | 16.7457 | 35 | 0.016 | 2 | NA | NA | 26.9071 | 0.019281 | 0.81335
54 | N | 0.225 | 0.006 | 0.3 | 1 | 1463.9304 | 7.54 | 16.7353 | 35 | 0.016 | 2 | NA | NA | 26.4492 | 0.019469 | 0.85869
55 | N | 0.25 | 0.006 | 0.3 | 1 | 1465.158 | 7.54 | 16.7288 | 35 | 0.016 | 2 | NA | NA | 26.1605 | 0.019587 | 0.88766
56 | N | 0.275 | 0.006 | 0.3 | 1 | 1466.5145 | 7.54 | 16.7216 | 35 | 0.016 | 2 | NA | NA | 25.842 | 0.019718 | 0.9204
57 | N | 0.3 | 0.006 | 0.3 | 1 | 1467.4057 | 7.54 | 16.7169 | 35 | 0.016 | 2 | NA | NA | 25.633 | 0.019804 | 0.94055
58 | N | 0.1 | 0.006 | 0.3 | 1 | 2166.0883 | 7.54 | 16.8422 | 35 | 0.016 | 3 | NA | NA | 31.1775 | 0.017545 | 0.38388
59 | N | 0.125 | 0.006 | 0.3 | 1 | 2173.6812 | 7.54 | 16.8148 | 35 | 0.016 | 3 | NA | NA | 29.9631 | 0.01804 | 0.50605
60 | N | 0.15 | 0.006 | 0.3 | 1 | 2179.6237 | 7.54 | 16.7934 | 35 | 0.016 | 3 | NA | NA | 29.0174 | 0.018422 | 0.6005
61 | N | 0.175 | 0.006 | 0.3 | 1 | 2184.963 | 7.54 | 16.7743 | 35 | 0.016 | 3 | NA | NA | 28.1713 | 0.018767 | 0.68615
62 | N | 0.2 | 0.006 | 0.3 | 1 | 2188.4922 | 7.54 | 16.7617 | 35 | 0.016 | 3 | NA | NA | 27.6139 | 0.018996 | 0.74156
63 | N | 0.225 | 0.006 | 0.3 | 1 | 2191.7776 | 7.54 | 16.75 | 35 | 0.016 | 3 | NA | NA | 27.0962 | 0.019203 | 0.79446
64 | N | 0.25 | 0.006 | 0.3 | 1 | 2194.0568 | 7.54 | 16.7419 | 35 | 0.016 | 3 | NA | NA | 26.7379 | 0.01935 | 0.82972
65 | N | 0.275 | 0.006 | 0.3 | 1 | 2196.3399 | 7.54 | 16.7338 | 35 | 0.016 | 3 | NA | NA | 26.3795 | 0.019497 | 0.86625
66 | N | 0.3 | 0.006 | 0.3 | 1 | 2198.4996 | 7.54 | 16.7261 | 35 | 0.016 | 3 | NA | NA | 26.0411 | 0.019636 | 0.90025
67 | N | 0.138 | 0.006 | 0.3 | 1 | 1489.7606 | 7.54 | 16.6973 | 35 | 0.0059507 | 2 | NA | NA | 24.1627 | 0.010327 | 0.63909
68 | N | 0.138 | 0.006 | 0.3 | 1 | 1484.3791 | 7.54 | 16.7133 | 35 | 0.0072018 | 2 | NA | NA | 24.9351 | 0.011222 | 0.62909
69 | N | 0.138 | 0.006 | 0.3 | 1 | 1480.0916 | 7.54 | 16.7231 | 35 | 0.0085059 | 2 | NA | NA | 25.4422 | 0.01233 | 0.63727
70 | N | 0.138 | 0.006 | 0.3 | 1 | 1474.738 | 7.54 | 16.7381 | 35 | 0.0098658 | 2 | NA | NA | 26.1815 | 0.01344 | 0.63091
71 | N | 0.138 | 0.006 | 0.3 | 1 | 1469.4916 | 7.54 | 16.752 | 35 | 0.011284 | 2 | NA | NA | 26.8817 | 0.014566 | 0.62545
72 | N | 0.138 | 0.006 | 0.3 | 1 | 1465.2812 | 7.54 | 16.7599 | 35 | 0.012765 | 2 | NA | NA | 27.3229 | 0.015896 | 0.64091
73 | N | 0.138 | 0.006 | 0.3 | 1 | 1459.667 | 7.54 | 16.7747 | 35 | 0.01431 | 2 | NA | NA | 28.0769 | 0.017096 | 0.62909
74 | N | 0.138 | 0.006 | 0.3 | 1 | 1455.0358 | 7.54 | 16.7837 | 35 | 0.015925 | 2 | NA | NA | 28.5804 | 0.0185 | 0.64091
75 | N | 0.138 | 0.006 | 0.3 | 1 | 1505.4373 | 7.54 | 16.6032 | 32 | 0.00718 | 2 | NA | NA | 23.1483 | 0.010743 | 0.63273
76 | N | 0.138 | 0.006 | 0.3 | 1 | 1501.1606 | 7.54 | 16.6131 | 32 | 0.0084362 | 2 | NA | NA | 23.6489 | 0.011749 | 0.64091
77 | N | 0.138 | 0.006 | 0.3 | 1 | 1495.4763 | 7.54 | 16.63 | 32 | 0.0097454 | 2 | NA | NA | 24.4547 | 0.012733 | 0.62727
78 | N | 0.138 | 0.006 | 0.3 | 1 | 1490.6393 | 7.54 | 16.642 | 32 | 0.011111 | 2 | NA | NA | 25.0542 | 0.013898 | 0.63091
79 | N | 0.138 | 0.006 | 0.3 | 1 | 1485.8603 | 7.54 | 16.6532 | 32 | 0.012535 | 2 | NA | NA | 25.6249 | 0.015074 | 0.63636
80 | N | 0.138 | 0.006 | 0.3 | 1 | 1480.4639 | 7.54 | 16.6671 | 32 | 0.014021 | 2 | NA | NA | 26.3214 | 0.016296 | 0.63
81 | N | 0.138 | 0.006 | 0.3 | 1 | 1475.1648 | 7.54 | 16.68 | 32 | 0.015572 | 2 | NA | NA | 26.9791 | 0.017634 | 0.62909
82 | N | 0.138 | 0.006 | 0.3 | 1 | 1469.8278 | 7.54 | 16.6925 | 32 | 0.017192 | 2 | NA | NA | 27.6279 | 0.018975 | 0.62455