## Chen2025
Paper information
Authors | Chen et al.
Title | A first-of-its-kind two-stage dew-point evaporative cooler with high energy efficiency and compact design
Year | 2025
Data type | Experimental, extracted from graphs
Description | Experimental test of a crossflow two-stage IEC designed to operate with only two fans. IEC and D-IEC sections both in crossflow configuration to extract the outlet secondary air streams with a single fan. Tests under various air flow rates but constant inlet air conditions. Better performance of the two-stage IEC than other D-IECs studies in the literature, while working with a lower SPR in the D-IEC section. Only the primary air flow rate and the air flow rate in the D-IEC section provided in the reference paper. To complete the dataset, assumption that the air velocity was similar in the D-IEC and the IEC sections.
EC characteristics |  |  | Configuration
EC type | 2-stage IEC |  | pd | sw_1 | pd | sw_2
EC 1 | IEC |  | Crossflow |  | Crossflow
EC 2 | D-IEC
Water injection type | Wet surface
Water recirculation | Yes
Wall material | NA
Configuration | XF/XF
Geometry |  |  |  | Measurement uncertainties
Length | 0.44 | m |  | Temperature | 0.21 | K
Width | 0.4 | m |  | Humidity | 2 | %
Height | 0.5 | m |  | Air flow | 0.03 | m/s
Channel height | 0.003 | m
Wall thickness | 0.0001 | m
Number of channels | 141 | -
Operating conditions
Primary fluid velocity | 0.5-4 | m/s
Secondary fluid velocity | 0.15-1.3 | m/s
Secondary-to-Primary flow rate ratio | 0.29-0.36 | kg/kg
Water supplied | NA | kg/s
| Testing conditions | [12 empty] | Inlet conditions | [10 empty] | Outlet conditions
Run | Test | L_1 | L_2 | h_ch | W | WWR | SPR_1 | SPR_2 | Re | Nu | h_T_pd | h_T_sw_1 | h_T_sw_2 | T_pdi | w_pdi | v_pdi | T_swi_1 | w_swi_1 | v_swi_1 | T_swi_2 | w_swi_2 | v_swi_2 | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo_1 | w_wso_1 | T_swo_2 | w_wso_2 | epsilon_wb | epsilon_dp
1 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.21557 | 0.0904 | 189.9164 | 7.54 | 33.5986 | 33.5986 | 32.8312 | 32.1938 | 0.017629 | 0.52426 | 32.1938 | 0.52426 | 0.14583 | 23.7241 | 0.017629 | 0.14583 | NA | NA | 23.7241 | 0.017629 | NA | NA | NA | NA | 1.2306 | 0.94216
2 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.20124 | 0.084393 | 343.1258 | 7.54 | 33.5985 | 33.5985 | 32.8653 | 32.2075 | 0.018062 | 0.9477 | 32.2075 | 0.9477 | 0.24609 | 24.1072 | 0.018062 | 0.24609 | NA | NA | 24.1072 | 0.018062 | NA | NA | NA | NA | 1.2206 | 0.93375
3 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.24493 | 0.10271 | 498.7784 | 7.54 | 33.6258 | 33.6258 | 32.8936 | 32.4949 | 0.017593 | 1.3792 | 32.4949 | 1.3792 | 0.43589 | 24.4082 | 0.017593 | 0.43589 | NA | NA | 24.4082 | 0.017593 | NA | NA | NA | NA | 1.1344 | 0.87946
4 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.24974 | 0.10473 | 637.517 | 7.54 | 33.6536 | 33.6536 | 32.9268 | 32.8096 | 0.01776 | 1.7664 | 32.8096 | 1.7664 | 0.56921 | 24.7777 | 0.01776 | 0.56921 | NA | NA | 24.7777 | 0.01776 | NA | NA | NA | NA | 1.1055 | 0.87092
5 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.21889 | 0.091794 | 811.5293 | 7.54 | 33.615 | 33.615 | 32.992 | 32.3717 | 0.017508 | 2.2422 | 32.3717 | 2.2422 | 0.6333 | 25.4892 | 0.017508 | 0.6333 | NA | NA | 25.4892 | 0.017508 | NA | NA | NA | NA | 0.97104 | 0.75639
6 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.23429 | 0.098251 | 1082.5656 | 7.54 | 33.6255 | 33.6255 | 33.0211 | 32.4812 | 0.017301 | 2.9923 | 32.4812 | 2.9923 | 0.90461 | 25.8039 | 0.017301 | 0.90461 | NA | NA | 25.8039 | 0.017301 | NA | NA | NA | NA | 0.91557 | 0.71554
7 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.23565 | 0.098819 | 1342.975 | 7.54 | 33.6341 | 33.6341 | 33.0385 | 32.577 | 0.017306 | 3.7142 | 32.577 | 3.7142 | 1.1293 | 25.9954 | 0.017306 | 1.1293 | NA | NA | 25.9954 | 0.017306 | NA | NA | NA | NA | 0.89405 | 0.69609
8 | E | 0.31 | 0.13 | 0.003 | 0.4 | 1 | 0.2494 | 0.10459 | 1460.0528 | 7.54 | 33.6584 | 33.6584 | 33.0586 | 32.8233 | 0.016635 | 4.0408 | 32.8233 | 4.0408 | 1.3004 | 26.2007 | 0.016635 | 1.3004 | NA | NA | 26.2007 | 0.016635 | NA | NA | NA | NA | 0.83305 | 0.64879