## Characteristics
Paper information
Authors | Nada et al.
Title | Experimental investigation of energy and exergy performance of a direct evaporative cooler using a new pad type
Year | 2019
Data type | Experimental, extracted from graphs
Description | Testing of a new evaporative cooling pad material made of cellulose corrugated sheets assembled in a “bee-hive” structure. Study of the thermal and hydraulic performance of the DEC for a wide range of operating conditions and geometric parameters. Modification of the cooling pad length by arranging 1 to 4 pads in series. Study of the impact of varying air velocity, inlet air temperature, and humidifier water temperature and flow rate.
HEX characteristics |  |  | Configuration
HEX type | DEC |  | pd | wf
Water injection type | Sprayed-water |  | Crossflow
Water recirculation | No
Wall material | Cellulose
Configuration | XF
Geometry |  |  |  | Measurement uncertainties
Length | 0.035 | m |  | Temperature | 1 | K
Width | 0.47 | m |  | Humidity | 5 | %
Height | 0.41 | m |  | Air flow | 1 | %
Channel height | 0.007 | m
Wall thickness | 0.0007 | m
Number of channels | 53 | - |  | Test
|  |  |  | A | Variable channel length
Operating conditions |  |  |  | B | Variable water flow rate
Primary fluid velocity | [1-3] | m/s |  | C | Variable water temperature
Water supplied | [0.0465-0.1667] | kg/s |  | D | Variable inlet air temperature

## Data
| Testing conditions | [7 empty] | Inlet conditions |  |  |  |  | Outlet conditions
Run | Test | L | h_ch | W | WWR | Re | Nu | h_T | T_pwi | w_pwi | v_pwi | T_wfi | m_dot_wf | T_pwo | w_pwo | epsilon_wb
1 | A | 0.035 | 0.007 | 0.47 | 1.1 | 743.3876 | 7.54 | 16.1915 | 40 | 0.0067935 | 1 | 30 | 0.0031453 | 27.7829 | 0.011822 | 0.61878
2 | A | 0.035 | 0.007 | 0.47 | 1.1 | 1114.5366 | 7.54 | 16.1905 | 40 | 0.0072587 | 1.5 | 30 | 0.0031453 | 28.9612 | 0.011761 | 0.56906
3 | A | 0.035 | 0.007 | 0.47 | 1.1 | 1485.2676 | 7.54 | 16.1895 | 40 | 0.0077598 | 2 | 30 | 0.0031453 | 29.9742 | 0.011867 | 0.5268
4 | A | 0.035 | 0.007 | 0.47 | 1.1 | 1857.8808 | 7.54 | 16.1908 | 40 | 0.0070948 | 2.5 | 30 | 0.0031453 | 31.5452 | 0.010362 | 0.43315
5 | A | 0.035 | 0.007 | 0.47 | 1.1 | 2229.6361 | 7.54 | 16.191 | 40 | 0.0070183 | 3 | 30 | 0.0031453 | 31.9587 | 0.010121 | 0.41077
6 | A | 0.07 | 0.007 | 0.47 | 1.1 | 744.2134 | 7.54 | 16.1936 | 40 | 0.0057372 | 1 | 30 | 0.0031453 | 26.0258 | 0.011441 | 0.68011
7 | A | 0.07 | 0.007 | 0.47 | 1.1 | 1116.2086 | 7.54 | 16.1934 | 40 | 0.0058322 | 1.5 | 30 | 0.0031453 | 27.5349 | 0.010927 | 0.60884
8 | A | 0.07 | 0.007 | 0.47 | 1.1 | 1488.4073 | 7.54 | 16.1936 | 40 | 0.0057497 | 2 | 30 | 0.0031453 | 27.9897 | 0.010614 | 0.58481
9 | A | 0.07 | 0.007 | 0.47 | 1.1 | 1859.6714 | 7.54 | 16.1927 | 40 | 0.0061779 | 2.5 | 30 | 0.0031453 | 29.0026 | 0.010647 | 0.5442
10 | A | 0.07 | 0.007 | 0.47 | 1.1 | 2231.2187 | 7.54 | 16.1924 | 40 | 0.0063429 | 3 | 30 | 0.0031453 | 30.0362 | 0.010417 | 0.49613
11 | A | 0.105 | 0.007 | 0.47 | 1.1 | 743.7275 | 7.54 | 16.1924 | 40 | 0.0063583 | 1 | 30 | 0.0031453 | 25.4677 | 0.012342 | 0.72403
12 | A | 0.105 | 0.007 | 0.47 | 1.1 | 1115.4434 | 7.54 | 16.1921 | 40 | 0.0064845 | 1.5 | 30 | 0.0031453 | 26.646 | 0.011941 | 0.66851
13 | A | 0.105 | 0.007 | 0.47 | 1.1 | 1487.1928 | 7.54 | 16.192 | 40 | 0.0065261 | 2 | 30 | 0.0031453 | 27.2455 | 0.011769 | 0.6395
14 | A | 0.105 | 0.007 | 0.47 | 1.1 | 1858.081 | 7.54 | 16.1911 | 40 | 0.0069922 | 2.5 | 30 | 0.0031453 | 28.5891 | 0.011725 | 0.58232
15 | A | 0.105 | 0.007 | 0.47 | 1.1 | 2230.0211 | 7.54 | 16.1913 | 40 | 0.0068539 | 3 | 30 | 0.0031453 | 29.0026 | 0.011372 | 0.55829
16 | A | 0.14 | 0.007 | 0.47 | 1.1 | 743.1102 | 7.54 | 16.1907 | 40 | 0.0071487 | 1 | 30 | 0.0031453 | 24.9922 | 0.013692 | 0.77044
17 | A | 0.14 | 0.007 | 0.47 | 1.1 | 1115.5609 | 7.54 | 16.1923 | 40 | 0.0063842 | 1.5 | 30 | 0.0031453 | 25.9638 | 0.012088 | 0.7
18 | A | 0.14 | 0.007 | 0.47 | 1.1 | 1485.9002 | 7.54 | 16.1903 | 40 | 0.007354 | 2 | 30 | 0.0031453 | 26.7907 | 0.012778 | 0.68343
19 | A | 0.14 | 0.007 | 0.47 | 1.1 | 1859.8338 | 7.54 | 16.1929 | 40 | 0.0060948 | 2.5 | 30 | 0.0031453 | 27.4729 | 0.011206 | 0.61796
20 | A | 0.14 | 0.007 | 0.47 | 1.1 | 2230.7019 | 7.54 | 16.1919 | 40 | 0.0065633 | 3 | 30 | 0.0031453 | 27.9897 | 0.01146 | 0.60304
21 | B | 0.07 | 0.007 | 0.47 | 1.1 | 743.7992 | 7.54 | 16.1925 | 40 | 0.0062666 | 1 | 30 | 0.00087736 | 27.9487 | 0.011211 | 0.59835
22 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1115.3295 | 7.54 | 16.1919 | 40 | 0.0065816 | 1.5 | 30 | 0.00087736 | 28.5026 | 0.011293 | 0.57769
23 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1489.4898 | 7.54 | 16.195 | 40 | 0.0050588 | 2 | 30 | 0.00087736 | 29.2 | 0.0095619 | 0.5124
24 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1858.164 | 7.54 | 16.1911 | 40 | 0.0069497 | 2.5 | 30 | 0.00087736 | 31.0462 | 0.010643 | 0.4562
25 | B | 0.07 | 0.007 | 0.47 | 1.1 | 2233.6102 | 7.54 | 16.1945 | 40 | 0.0053243 | 3 | 30 | 0.00087736 | 31.4974 | 0.0085759 | 0.40744
26 | B | 0.07 | 0.007 | 0.47 | 1.1 | 743.8449 | 7.54 | 16.1927 | 40 | 0.0062082 | 1 | 30 | 0.0017962 | 27.5385 | 0.011325 | 0.61736
27 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1115.806 | 7.54 | 16.1927 | 40 | 0.0061753 | 1.5 | 30 | 0.0017962 | 28.1744 | 0.011022 | 0.58512
28 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1489.3429 | 7.54 | 16.1948 | 40 | 0.0051525 | 2 | 30 | 0.0017962 | 28.9949 | 0.0096678 | 0.52397
29 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1858.7958 | 7.54 | 16.1918 | 40 | 0.006626 | 2.5 | 30 | 0.0017962 | 30.4103 | 0.010736 | 0.48264
30 | B | 0.07 | 0.007 | 0.47 | 1.1 | 2232.2607 | 7.54 | 16.1933 | 40 | 0.0058988 | 3 | 30 | 0.0017962 | 31.1897 | 0.0093835 | 0.4314
31 | B | 0.07 | 0.007 | 0.47 | 1.1 | 743.7803 | 7.54 | 16.1925 | 40 | 0.0062907 | 1 | 30 | 0.0022189 | 27.1282 | 0.011505 | 0.63967
32 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1115.7019 | 7.54 | 16.1925 | 40 | 0.006264 | 1.5 | 30 | 0.0022189 | 28.0308 | 0.011319 | 0.59421
33 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1489.4994 | 7.54 | 16.195 | 40 | 0.0050527 | 2 | 30 | 0.0022189 | 28.6051 | 0.0097521 | 0.5405
34 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1861.7423 | 7.54 | 16.1949 | 40 | 0.00512 | 2.5 | 30 | 0.0022189 | 29.5897 | 0.0092427 | 0.49504
35 | B | 0.07 | 0.007 | 0.47 | 1.1 | 2231.1849 | 7.54 | 16.1924 | 40 | 0.0063573 | 3 | 30 | 0.0022189 | 31.0256 | 0.010051 | 0.44711
36 | B | 0.07 | 0.007 | 0.47 | 1.1 | 744.2857 | 7.54 | 16.1938 | 40 | 0.0056448 | 1 | 30 | 0.0031453 | 25.959 | 0.011363 | 0.68099
37 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1116.3404 | 7.54 | 16.1937 | 40 | 0.0057199 | 1.5 | 30 | 0.0031453 | 27.4769 | 0.010861 | 0.60909
38 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1487.898 | 7.54 | 16.1929 | 40 | 0.0060751 | 2 | 30 | 0.0031453 | 28.1128 | 0.010922 | 0.58595
39 | B | 0.07 | 0.007 | 0.47 | 1.1 | 1859.6669 | 7.54 | 16.1927 | 40 | 0.0061802 | 2.5 | 30 | 0.0031453 | 28.9949 | 0.010671 | 0.54463
40 | B | 0.07 | 0.007 | 0.47 | 1.1 | 2231.477 | 7.54 | 16.1926 | 40 | 0.0062328 | 3 | 30 | 0.0031453 | 30 | 0.010331 | 0.49587
41 | C | 0.07 | 0.007 | 0.47 | 1.1 | 745.2865 | 7.54 | 16.1964 | 40 | 0.0043686 | 1 | 25 | 0.0031453 | 21.971 | 0.011757 | 0.83354
42 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1117.002 | 7.54 | 16.1948 | 40 | 0.0051569 | 1.5 | 25 | 0.0031453 | 22.5217 | 0.012312 | 0.8323
43 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1488.6369 | 7.54 | 16.1939 | 40 | 0.005603 | 2 | 25 | 0.0031453 | 23.7101 | 0.012263 | 0.78882
44 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1860.5923 | 7.54 | 16.1937 | 40 | 0.0057071 | 2.5 | 25 | 0.0031453 | 24.4638 | 0.012018 | 0.75528
45 | C | 0.07 | 0.007 | 0.47 | 1.1 | 2231.477 | 7.54 | 16.1926 | 40 | 0.0062328 | 3 | 25 | 0.0031453 | 25.971 | 0.011946 | 0.69565
46 | C | 0.07 | 0.007 | 0.47 | 1.1 | 744.1841 | 7.54 | 16.1935 | 40 | 0.0057746 | 1 | 30 | 0.0031453 | 26.058 | 0.011488 | 0.6795
47 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1116.2037 | 7.54 | 16.1934 | 40 | 0.0058364 | 1.5 | 30 | 0.0031453 | 27.5652 | 0.010953 | 0.60745
48 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1487.8332 | 7.54 | 16.1928 | 40 | 0.0061165 | 2 | 30 | 0.0031453 | 28.1739 | 0.010985 | 0.58385
49 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1859.7432 | 7.54 | 16.1928 | 40 | 0.0061412 | 2.5 | 30 | 0.0031453 | 29.0145 | 0.010632 | 0.54286
50 | C | 0.07 | 0.007 | 0.47 | 1.1 | 2231.3485 | 7.54 | 16.1925 | 40 | 0.0062875 | 3 | 30 | 0.0031453 | 30 | 0.01037 | 0.49689
51 | C | 0.07 | 0.007 | 0.47 | 1.1 | 744.3219 | 7.54 | 16.1939 | 40 | 0.0055986 | 1 | 35 | 0.0031453 | 33.0725 | 0.0084579 | 0.3354
52 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1116.1449 | 7.54 | 16.1933 | 40 | 0.0058864 | 1.5 | 35 | 0.0031453 | 35.1015 | 0.0079301 | 0.23975
53 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1487.9707 | 7.54 | 16.193 | 40 | 0.0060286 | 2 | 35 | 0.0031453 | 36.087 | 0.0076791 | 0.19255
54 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1859.8798 | 7.54 | 16.1929 | 40 | 0.0060713 | 2.5 | 35 | 0.0031453 | 37.1014 | 0.0072995 | 0.14286
55 | C | 0.07 | 0.007 | 0.47 | 1.1 | 2232.9254 | 7.54 | 16.1939 | 40 | 0.0056158 | 3 | 35 | 0.0031453 | 37.3333 | 0.0067129 | 0.12919
56 | C | 0.07 | 0.007 | 0.47 | 1.1 | 744.3219 | 7.54 | 16.1939 | 40 | 0.0055986 | 1 | 40 | 0.0031453 | 39.4203 | 0.0058656 | 0.024845
57 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1116.1449 | 7.54 | 16.1933 | 40 | 0.0058864 | 1.5 | 40 | 0.0031453 | 39.5072 | 0.0061097 | 0.018634
58 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1487.9707 | 7.54 | 16.193 | 40 | 0.0060286 | 2 | 40 | 0.0031453 | 39.7391 | 0.0061354 | 0.0074534
59 | C | 0.07 | 0.007 | 0.47 | 1.1 | 1859.8798 | 7.54 | 16.1929 | 40 | 0.0060713 | 2.5 | 40 | 0.0031453 | 39.7391 | 0.0061781 | 0.0086957
60 | C | 0.07 | 0.007 | 0.47 | 1.1 | 2232.9254 | 7.54 | 16.1939 | 40 | 0.0056158 | 3 | 40 | 0.0031453 | 39.8841 | 0.0056158 | 0.002
61 | D | 0.07 | 0.007 | 0.47 | 1.1 | 788.8469 | 7.54 | 15.7625 | 30 | 0.0050655 | 1 | 30 | 0.0031453 | 21.075 | 0.0087975 | 0.61538
62 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1183.1308 | 7.54 | 15.7624 | 30 | 0.0051741 | 1.5 | 30 | 0.0031453 | 22.525 | 0.0082875 | 0.51888
63 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1577.1594 | 7.54 | 15.7621 | 30 | 0.0053775 | 2 | 30 | 0.0031453 | 23.55 | 0.0080579 | 0.45343
64 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1965.1369 | 7.54 | 15.7582 | 30 | 0.0083375 | 2.5 | 30 | 0.0031453 | 25.075 | 0.010399 | 0.41986
65 | D | 0.07 | 0.007 | 0.47 | 1.1 | 2361.214 | 7.54 | 15.7597 | 30 | 0.0071431 | 3 | 30 | 0.0031453 | 25.55 | 0.0089988 | 0.35021
66 | D | 0.07 | 0.007 | 0.47 | 1.1 | 768.2192 | 7.54 | 15.9833 | 35 | 0.0027069 | 1 | 30 | 0.0031453 | 22.45 | 0.0078615 | 0.63385
67 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1151.5017 | 7.54 | 15.9822 | 35 | 0.0033764 | 1.5 | 30 | 0.0031453 | 24.025 | 0.0078918 | 0.57175
68 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1534.6622 | 7.54 | 15.9815 | 35 | 0.0037858 | 2 | 30 | 0.0031453 | 24.975 | 0.0078889 | 0.53231
69 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1915.3186 | 7.54 | 15.979 | 35 | 0.0052527 | 2.5 | 30 | 0.0031453 | 26.175 | 0.0088815 | 0.5021
70 | D | 0.07 | 0.007 | 0.47 | 1.1 | 2299.8627 | 7.54 | 15.98 | 35 | 0.0046507 | 3 | 30 | 0.0031453 | 27.225 | 0.0078672 | 0.42993
71 | D | 0.07 | 0.007 | 0.47 | 1.1 | 744.1692 | 7.54 | 16.1935 | 40 | 0.0057937 | 1 | 30 | 0.0031453 | 26.075 | 0.011546 | 0.67916
72 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1116.097 | 7.54 | 16.1932 | 40 | 0.0059273 | 1.5 | 30 | 0.0031453 | 27.6 | 0.01102 | 0.60783
73 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1488.351 | 7.54 | 16.1935 | 40 | 0.0057856 | 2 | 30 | 0.0031453 | 28.05 | 0.010693 | 0.58266
74 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1859.5447 | 7.54 | 16.1926 | 40 | 0.0062427 | 2.5 | 30 | 0.0031453 | 29.1 | 0.010779 | 0.5407
75 | D | 0.07 | 0.007 | 0.47 | 1.1 | 2231.2807 | 7.54 | 16.1924 | 40 | 0.0063165 | 3 | 30 | 0.0031453 | 30.075 | 0.010461 | 0.49371
76 | D | 0.07 | 0.007 | 0.47 | 1.1 | 723.6494 | 7.54 | 16.4079 | 45 | 0.0057471 | 1 | 30 | 0.0031453 | 27.95 | 0.012675 | 0.71021
77 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1084.8803 | 7.54 | 16.4066 | 45 | 0.0062757 | 1.5 | 30 | 0.0031453 | 28.975 | 0.012832 | 0.67832
78 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1446.2666 | 7.54 | 16.4062 | 45 | 0.0064364 | 2 | 30 | 0.0031453 | 30 | 0.012581 | 0.63804
79 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1807.3575 | 7.54 | 16.4056 | 45 | 0.0066908 | 2.5 | 30 | 0.0031453 | 31.525 | 0.012217 | 0.57762
80 | D | 0.07 | 0.007 | 0.47 | 1.1 | 2168.6575 | 7.54 | 16.4054 | 45 | 0.0067673 | 3 | 30 | 0.0031453 | 32.65 | 0.011819 | 0.53063
81 | D | 0.07 | 0.007 | 0.47 | 1.1 | 700.8204 | 7.54 | 16.6087 | 50 | 0.010194 | 1 | 30 | 0.0031453 | 31.975 | 0.017617 | 0.73035
82 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1050.143 | 7.54 | 16.6059 | 50 | 0.011215 | 1.5 | 30 | 0.0031453 | 33.15 | 0.018061 | 0.70014
83 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1399.4448 | 7.54 | 16.6045 | 50 | 0.011742 | 2 | 30 | 0.0031453 | 33.925 | 0.018072 | 0.67664
84 | D | 0.07 | 0.007 | 0.47 | 1.1 | 1749.5571 | 7.54 | 16.6049 | 50 | 0.0116 | 2.5 | 30 | 0.0031453 | 35.475 | 0.018985 | 0.63133
85 | D | 0.07 | 0.007 | 0.47 | 1.1 | 2100.4619 | 7.54 | 16.6061 | 50 | 0.011133 | 3 | 30 | 0.0031453 | 36.475 | 0.0167 | 0.56084