## Characteristics
Paper information
Authors | Ren & Yang
Title | An analytical model for the heat and mass transfer processes in indirect evaporative cooling with parallel/counter flow configurations
Year | 2006
Data type | Numerical and analytical, raw data, under the format used in the paper
Description | Ren & Yang proposed a set of differential equations for the primary air and water film temperatures and for the secondary air temperature and humidity ratio, using dimensionless coefficients for parallel and counterflow configurations. Results provided for the analytical model resolution and the numerical model for various coefficient combinations. NB: The use of this dataset is relevant only if the formalism of the numerical model is similar to the one proposed by Ren and Yang.
HEX characteristics |  |  | Configuration
HEX type | IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Water film |  | parallel |  | counterflow |  | counterflow
Water recirculation | Yes
Configuration | PPC
Geometry |  |  |  | Important note : For the nomenclature refer to the original paper
Length | NA | m
Width | NA | m
Height | NA | m
Channel width | NA | m
Wall thickness | NA | m
Number of channels | NA | -
Operating conditions
Primary fluid velocity | NA
Secondary fluid velocity | NA
Secondary-to-Primary flow rate ratio | NA | kg/kg
Water supplied | NA

## Data
| Given conditions | [7 empty] | Analytical results |  |  | Numerical results
Run | T_pdi | T_swi | w_swi | C_star_w | C_star_f | r | sigma_Lef | NTU | T_pdo | T_swo | w_swo | T_pdo | T_swo | w_swo
1 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 0.8 | 3 | 30.36 | 28.36 | 0.0239 | 30.35 | 28.35 | 0.0239
2 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 0.8 | 1 | 33.46 | 28.27 | 0.0201 | 33.45 | 28.26 | 0.0201
3 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 0.5 | 2 | 32.07 | 28.66 | 0.02166 | 32.07 | 28.65 | 0.02166
4 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 1.1 | 2 | 31.45 | 27.74 | 0.02281 | 31.45 | 27.74 | 0.02281
5 | 36 | 30 | 0.01622 | 0 | 3 | 2.8 | 0.8 | 2 | 29.31 | 29.66 | 0.02466 | 29.3 | 29.66 | 0.02466
6 | 36 | 30 | 0.01622 | 0 | 0.75 | 1 | 0.8 | 2 | 25.87 | 26.77 | 0.02072 | 25.85 | 26.77 | 0.02072
7 | 36 | 30 | 0.01622 | 0.5 | 3 | 1 | 0.8 | 3 | 30.46 | 28.26 | 0.02382 | 30.45 | 28.24 | 0.0238
8 | 36 | 30 | 0.01622 | 0.5 | 3 | 8 | 0.8 | 3 | 26.73 | 30.65 | 0.02744 | 26.7 | 30.63 | 0.0274
9 | 36 | 30 | 0.01622 | 1 | 3 | 1 | 1 | 5 | 28.78 | 28.84 | 0.02565 | 28.77 | 28.8 | 0.02562
10 | 36 | 30 | 0.01622 | 4 | 3 | 8 | 1 | 2 | 28.55 | 29.7 | 0.02559 | 28.56 | 29.7 | 0.02554
11 | 50 | 35 | 0.02171 | 4 | 3 | 8 | 1 | 2 | 34.97 | 36.86 | 0.0397 | 35.02 | 36.87 | 0.03951
12 | 21 | 21 | 0.00941 | 4 | 3 | 8 | 1 | 2 | 18.5 | 19.16 | 0.01325 | 18.49 | 19.16 | 0.01325
13 | 21 | 21 | 0.00941 | 4 | 3 | 8 | 1 | 3 | 18.25 | 18.97 | 0.01363 | 18.25 | 18.97 | 0.01362
14 | 21 | 21 | 0.00941 | 4 | 3 | 8 | 1 | 1 | 19.06 | 19.75 | 0.01231 | 19.06 | 19.75 | 0.0123
15 | 36 | 30 | 0.01622 | 4 | 12 | 8 | 1 | 2 | 33.11 | 32.05 | 0.02972 | 33.11 | 32.04 | 0.02969
16 | 36 | 30 | 0.01622 | 4 | 3 | 8 | 1.1 | 2 | 28.43 | 29.63 | 0.02576 | 28.45 | 29.63 | 0.02571