## Riangvilaikul2010
Paper information
Authors | Riangvilaikul and Kumar
Title | An experimental study of a novel dew point evaporative cooling system
Year | 2010
Data type | Experimental, extracted from graphs
Description | Counterflow D-IEC made of vertical thin-film cotton sheets coated with polyurethane material. Water is sprayed on top of the wet channel, and the water distribution on the wet channel surface is ensured through gravitational effect. Advantages of the dataset provided: 1. Independent testing of the impact of primary inlet air conditions and velocity on the primary outlet temperature. 2. The tested inlet air conditions cover a large area of the psychrometric diagram.
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | sw | pd | sw | sw | wf
Water injection type | Wet surface theory |  | parallel |  | counterflow |  | counterflow
Water recirculation | Yes
Wall material | Cotton sheet coated with polyurethane
Configuration | PPC
Geometry |  |  |  | Measurement uncertainties
Length | 1.2 | m |  | Temperature | 2 | K
Width | 0.08 | m |  | Humidity | NA | %
Height | 0.05 | m |  | Air flow | 5 | %
Channel height | 0.005 | m
Wall thickness | 0.0005 | m
Number of channels | 9 | -
Operating conditions |  |  |  | Tests
Primary fluid velocity | 1.45-6 | m/s |  | A | Constant velocity & Varying inlet conditions
Secondary fluid velocity | 0.48-1.98 | m/s |  | B | Constant inlet conditions & Varying inlet velocity
Secondary-to-Primary flow rate ratio | 0.33 | kg/kg
Water supplied | 60 | g/h

## Data
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1572.6851 | 8.23 | 21.3076 | 21.3076 | 25 | 0.0069 | 2.4 | 15.6383 | 0.0069 | 0.792 | NA | 3.3333e-06 | 15.6383 | 0.0069 | NA | NA | 0.96562 | 0.566
2 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1544.5969 | 8.23 | 21.4893 | 21.4893 | 30.0213 | 0.0069 | 2.4 | 16.5957 | 0.0069 | 0.792 | NA | 3.3333e-06 | 16.5957 | 0.0069 | NA | NA | 1.0384 | 0.62254
3 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1518.5317 | 8.23 | 21.6622 | 21.6622 | 35.0107 | 0.0069 | 2.4 | 17.3138 | 0.0069 | 0.792 | NA | 3.3333e-06 | 17.3138 | 0.0069 | NA | NA | 1.0896 | 0.66674
4 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1493.5905 | 8.23 | 21.8316 | 21.8316 | 39.9041 | 0.0069 | 2.4 | 18.0319 | 0.0069 | 0.792 | NA | 3.3333e-06 | 18.0319 | 0.0069 | NA | NA | 1.1161 | 0.69568
5 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1468.6893 | 8.23 | 22.0049 | 22.0049 | 45.0213 | 0.0069 | 2.4 | 18.6702 | 0.0069 | 0.792 | NA | 3.3333e-06 | 18.6702 | 0.0069 | NA | NA | 1.136 | 0.72079
6 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1548.4842 | 8.23 | 21.4112 | 21.4112 | 24.8081 | 0.0112 | 2.4 | 19.3883 | 0.0112 | 0.792 | NA | 3.3333e-06 | 19.3883 | 0.0112 | NA | NA | 0.90658 | 0.59545
7 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1519.5586 | 8.23 | 21.6014 | 21.6014 | 30.0853 | 0.0112 | 2.4 | 20.4255 | 0.0112 | 0.792 | NA | 3.3333e-06 | 20.4255 | 0.0112 | NA | NA | 1.0062 | 0.67165
8 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1494.4387 | 8.23 | 21.7708 | 21.7708 | 35.0107 | 0.0112 | 2.4 | 21.1436 | 0.0112 | 0.792 | NA | 3.3333e-06 | 21.1436 | 0.0112 | NA | NA | 1.0616 | 0.71856
9 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1466.7091 | 8.23 | 21.9626 | 21.9626 | 40.5437 | 0.0112 | 2.4 | 22.0213 | 0.0112 | 0.792 | NA | 3.3333e-06 | 22.0213 | 0.0112 | NA | NA | 1.086 | 0.7458
10 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1444.3758 | 8.23 | 22.1208 | 22.1208 | 45.0533 | 0.0112 | 2.4 | 22.8191 | 0.0112 | 0.792 | NA | 3.3333e-06 | 22.8191 | 0.0112 | NA | NA | 1.0912 | 0.75761
11 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1479.8404 | 8.23 | 21.7599 | 21.7599 | 30.0213 | 0.02 | 2.4 | 26.25 | 0.02 | 0.792 | NA | 3.3333e-06 | 26.25 | 0.02 | NA | NA | 0.97558 | 0.7306
12 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1456.1495 | 8.23 | 21.9236 | 21.9236 | 35.0107 | 0.02 | 2.4 | 26.8085 | 0.02 | 0.792 | NA | 3.3333e-06 | 26.8085 | 0.02 | NA | NA | 1.0701 | 0.80787
13 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1431.758 | 8.23 | 22.0961 | 22.0961 | 40 | 0.02 | 2.4 | 27.6862 | 0.02 | 0.792 | NA | 3.3333e-06 | 27.6862 | 0.02 | NA | NA | 1.0689 | 0.81307
14 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1408.2133 | 8.23 | 22.2666 | 22.2666 | 45.0213 | 0.02 | 2.4 | 28.484 | 0.02 | 0.792 | NA | 3.3333e-06 | 28.484 | 0.02 | NA | NA | 1.0709 | 0.82043
15 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1444.2333 | 8.23 | 21.9263 | 21.9263 | 32.3241 | 0.0264 | 2.4 | 30 | 0.0264 | 0.792 | NA | 3.3333e-06 | 30 | 0.0264 | NA | NA | 1.0163 | 0.80046
16 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1429.2574 | 8.23 | 22.0319 | 22.0319 | 35.3945 | 0.0264 | 2.4 | 30.5585 | 0.0264 | 0.792 | NA | 3.3333e-06 | 30.5585 | 0.0264 | NA | NA | 1.0238 | 0.80927
17 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1405.9551 | 8.23 | 22.1995 | 22.1995 | 40.2878 | 0.0264 | 2.4 | 31.4362 | 0.0264 | 0.792 | NA | 3.3333e-06 | 31.4362 | 0.0264 | NA | NA | 1.0245 | 0.81429
18 | A | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1384.9391 | 8.23 | 22.354 | 22.354 | 44.9893 | 0.0264 | 2.4 | 32.0745 | 0.0264 | 0.792 | NA | 3.3333e-06 | 32.0745 | 0.0264 | NA | NA | 1.039 | 0.82989
19 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 935.1844 | 8.23 | 21.7124 | 21.7124 | 34 | 0.0112 | 1.4933 | 20.2062 | 0.0112 | 0.49278 | NA | 3.3333e-06 | 20.2062 | 0.0112 | NA | NA | 1.1168 | 0.75386
20 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1485.4811 | 8.23 | 21.734 | 21.734 | 34 | 0.0112 | 2.377 | 20.9278 | 0.0112 | 0.78442 | NA | 3.3333e-06 | 20.9278 | 0.0112 | NA | NA | 1.0585 | 0.7145
21 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 2033.9431 | 8.23 | 21.768 | 21.768 | 34 | 0.0112 | 3.2655 | 22.0619 | 0.0112 | 1.0776 | NA | 3.3333e-06 | 22.0619 | 0.0112 | NA | NA | 0.967 | 0.65273
22 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 2626.6253 | 12.2933 | 32.5914 | 21.819 | 34 | 0.0112 | 4.2382 | 23.7629 | 0.0112 | 1.3986 | NA | 3.3333e-06 | 23.7629 | 0.0112 | NA | NA | 0.82932 | 0.55979
23 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 3186.0583 | 15.3774 | 40.8083 | 21.8406 | 34 | 0.0112 | 5.1517 | 24.4845 | 0.0112 | 1.7001 | NA | 3.3333e-06 | 24.4845 | 0.0112 | NA | NA | 0.771 | 0.52043
24 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 3602.6847 | 17.5201 | 46.5371 | 21.8606 | 34 | 0.0112 | 5.8368 | 25.1546 | 0.0112 | 1.9262 | NA | 3.3333e-06 | 25.1546 | 0.0112 | NA | NA | 0.71674 | 0.48381
25 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 883.6698 | 8.23 | 21.862 | 21.862 | 34 | 0.019 | 1.4459 | 25.6701 | 0.019 | 0.47713 | NA | 3.3333e-06 | 25.6701 | 0.019 | NA | NA | 1.1185 | 0.83546
26 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1432.9273 | 8.23 | 21.8833 | 21.8833 | 34 | 0.019 | 2.3495 | 26.3918 | 0.019 | 0.77533 | NA | 3.3333e-06 | 26.3918 | 0.019 | NA | NA | 1.0218 | 0.76324
27 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 1980.5086 | 8.23 | 21.9016 | 21.9016 | 34 | 0.019 | 3.2531 | 27.0103 | 0.019 | 1.0735 | NA | 3.3333e-06 | 27.0103 | 0.019 | NA | NA | 0.93853 | 0.70106
28 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 2584.0858 | 12.0542 | 32.1185 | 21.929 | 34 | 0.019 | 4.256 | 27.9381 | 0.019 | 1.4045 | NA | 3.3333e-06 | 27.9381 | 0.019 | NA | NA | 0.81366 | 0.60779
29 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 3099.9194 | 14.9309 | 39.8001 | 21.9381 | 34 | 0.019 | 5.1101 | 28.2474 | 0.019 | 1.6863 | NA | 3.3333e-06 | 28.2474 | 0.019 | NA | NA | 0.77204 | 0.5767
30 | B | 1.2 | 0.005 | 0.08 | 1 | 0.33 | 3643.8152 | 17.7407 | 47.3162 | 21.9503 | 34 | 0.019 | 6.0139 | 28.6598 | 0.019 | 1.9846 | NA | 3.3333e-06 | 28.6598 | 0.019 | NA | NA | 0.71699 | 0.53557