## Characteristics
Paper information
Authors | Pakari & Ghani
Title | Regression models for performance prediction of counter ﬂow dew point evaporative cooling systems
Year | 2019
Data type | Experimental data (extracted from graphs) and numerical data (from table)
Description | Numerically testing of 90 combinations of geometrical parameters and operating conditions to evaluate the performance of D-IEC. Validation of the model performed with a vertical 100-channel D-IEC with dry channels made of corrugated plastic sheets stacked next to each other, and wicking paper pasted on the wet channels to enhance their wettability. Cooling system tested by varying the primary air extraction ratio and the inlet air conditions (temperature, relative humidity, and velocity).
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Wet surface theory |  | counterflow |  | counterflow |  | parallel
Water recirculation | Yes
Wall material | Plastic sheets
Configuration | PCC
Geometry |  |  |  | Measurement uncertainties
Length | 0.5 | m |  | Temperature | 0.2 | K
Width | 0.3 | m |  | Humidity | 4.6512 | %
Height | 0.22 | m |  | Air flow | 5.8824 | %
Channel height | 0.002 | m
Wall thickness | 0.0002 | m
Number of channels | 100 | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 0.5-1.5 | m/s |  | E | Experimental
Secondary fluid velocity | 0.15-0.52 | m/s |  | N | Numerical
Secondary-to-Primary flow rate ratio | 0.15-0.5 | kg/kg
Water supplied | NA | kg/s

## Data
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | E | 0.5 | 0.002 | 0.3 | 1 | 0.332 | 2.81 | 2.81 | 18.3515 | 49.2422 | 29.2 | 0.01094 | 0.59 | 17.9096 | 0.01094 | 0.19588 | NA | NA | 17.9096 | 0.01094 | NA | NA | 1.2305 | 0.81509
2 | E | 0.5 | 0.002 | 0.3 | 1 | 0.447 | 2.81 | 2.81 | 18.337 | 49.2033 | 30.1 | 0.0080015 | 0.55 | 16.3321 | 0.0080015 | 0.24585 | NA | NA | 16.3321 | 0.0080015 | NA | NA | 1.1409 | 0.70748
3 | E | 0.5 | 0.002 | 0.3 | 1 | 0.236 | 2.81 | 2.81 | 18.4096 | 49.3979 | 30.2 | 0.00832 | 0.82 | 19.0528 | 0.00832 | 0.19352 | NA | NA | 19.0528 | 0.00832 | NA | NA | 0.93847 | 0.58727
4 | E | 0.5 | 0.002 | 0.3 | 1 | 0.38 | 2.81 | 2.81 | 18.3681 | 49.2867 | 30.3 | 0.008095 | 0.62 | 17.3381 | 0.008095 | 0.2356 | NA | NA | 17.3381 | 0.008095 | NA | NA | 1.069 | 0.66511
5 | E | 0.5 | 0.002 | 0.3 | 1 | 0.37 | 2.81 | 2.81 | 18.4414 | 49.4833 | 30.3 | 0.0091903 | 0.87 | 20.2265 | 0.0091903 | 0.3219 | NA | NA | 20.2265 | 0.0091903 | NA | NA | 0.89468 | 0.57254
6 | E | 0.5 | 0.002 | 0.3 | 1 | 0.172 | 2.81 | 2.81 | 18.5788 | 49.852 | 30.5 | 0.0092978 | 0.95 | 25.3783 | 0.0092978 | 0.1634 | NA | NA | 25.3783 | 0.0092978 | NA | NA | 0.45276 | 0.29068
7 | E | 0.5 | 0.002 | 0.3 | 1 | 0.359 | 2.81 | 2.81 | 18.6002 | 49.9094 | 32.4 | 0.017593 | 0.57 | 24.7763 | 0.017593 | 0.20463 | NA | NA | 24.7763 | 0.017593 | NA | NA | 1.0801 | 0.79338
8 | E | 0.5 | 0.002 | 0.3 | 1 | 0.367 | 2.81 | 2.81 | 18.555 | 49.7881 | 35.1 | 0.0099283 | 0.54 | 19.8835 | 0.0099283 | 0.19818 | NA | NA | 19.8835 | 0.0099283 | NA | NA | 1.0849 | 0.71677
9 | E | 0.5 | 0.002 | 0.3 | 1 | 0.322 | 2.81 | 2.81 | 18.6785 | 50.1196 | 36.8 | 0.011712 | 0.58 | 23.1149 | 0.011712 | 0.18676 | NA | NA | 23.1149 | 0.011712 | NA | NA | 0.97745 | 0.67068
10 | E | 0.5 | 0.002 | 0.3 | 1 | 0.369 | 2.81 | 2.81 | 18.5893 | 49.8803 | 38.2 | 0.0092317 | 0.51 | 18.0849 | 0.0092317 | 0.18819 | NA | NA | 18.0849 | 0.0092317 | NA | NA | 1.2039 | 0.79109
11 | E | 0.5 | 0.002 | 0.3 | 1 | 0.376 | 2.81 | 2.81 | 18.7936 | 50.4283 | 40.2 | 0.015088 | 0.83 | 24.4638 | 0.015088 | 0.31208 | NA | NA | 24.4638 | 0.015088 | NA | NA | 1.0933 | 0.79262
12 | E | 0.5 | 0.002 | 0.3 | 1 | 0.483 | 2.81 | 2.81 | 18.7685 | 50.361 | 42.2 | 0.0093493 | 0.67 | 21.0876 | 0.0093493 | 0.32361 | NA | NA | 21.0876 | 0.0093493 | NA | NA | 1.0835 | 0.72212
13 | E | 0.5 | 0.002 | 0.3 | 1 | 0.308 | 2.81 | 2.81 | 18.8875 | 50.6805 | 43.9 | 0.011389 | 0.59 | 24.2047 | 0.011389 | 0.18172 | NA | NA | 24.2047 | 0.011389 | NA | NA | 1.0152 | 0.70502
14 | E | 0.5 | 0.002 | 0.3 | 1 | 0.417 | 2.81 | 2.81 | 18.8673 | 50.6263 | 44.1 | 0.014454 | 0.77 | 23.4349 | 0.014454 | 0.32109 | NA | NA | 23.4349 | 0.014454 | NA | NA | 1.1669 | 0.84587
15 | E | 0.5 | 0.002 | 0.3 | 1 | 0.337 | 2.81 | 2.81 | 18.8137 | 50.4823 | 44.2 | 0.0098076 | 0.55 | 20.8895 | 0.0098076 | 0.18535 | NA | NA | 20.8895 | 0.0098076 | NA | NA | 1.1298 | 0.76392
16 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
17 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7195 | 36.8131 | 40.25 | 0.019028 | 0.75 | 27.5 | 0.019028 | 0.17812 | NA | NA | 27.5 | 0.019028 | NA | NA | 1.05 | 0.78717
18 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7414 | 36.8718 | 40.25 | 0.019028 | 0.75 | 28.7 | 0.019028 | 0.17812 | NA | NA | 28.7 | 0.019028 | NA | NA | 0.94 | 0.71309
19 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
20 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4004 | 35.957 | 30.75 | 0.0055148 | 1.25 | 19 | 0.0055148 | 0.51562 | NA | NA | 19 | 0.0055148 | NA | NA | 0.81 | 0.4605
21 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.727 | 36.8334 | 40.25 | 0.0093704 | 1.25 | 27.2 | 0.0093704 | 0.29688 | NA | NA | 27.2 | 0.0093704 | NA | NA | 0.72 | 0.47886
22 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
23 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.7122 | 36.7935 | 40.25 | 0.019028 | 0.75 | 27.1 | 0.019028 | 0.30937 | NA | NA | 27.1 | 0.019028 | NA | NA | 1.07 | 0.81187
24 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8474 | 23.74 | 40.25 | 0.0093704 | 0.75 | 24.3 | 0.0093704 | 0.30937 | NA | NA | 24.3 | 0.0093704 | NA | NA | 0.88 | 0.58527
25 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.928 | 23.9563 | 40.25 | 0.019028 | 1.25 | 31.8 | 0.019028 | 0.51562 | NA | NA | 31.8 | 0.019028 | NA | NA | 0.69 | 0.52169
26 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7258 | 23.4136 | 30.75 | 0.011128 | 1.25 | 23.8 | 0.011128 | 0.29688 | NA | NA | 23.8 | 0.011128 | NA | NA | 0.69 | 0.45902
27 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6757 | 23.2794 | 30.75 | 0.0055148 | 1.25 | 19.4 | 0.0055148 | 0.51562 | NA | NA | 19.4 | 0.0055148 | NA | NA | 0.78 | 0.44482
28 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.6733 | 23.2729 | 30.75 | 0.0055148 | 0.75 | 19.2 | 0.0055148 | 0.17812 | NA | NA | 19.2 | 0.0055148 | NA | NA | 0.79 | 0.45266
29 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
30 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4294 | 36.0347 | 30.75 | 0.011128 | 1.25 | 20.8 | 0.011128 | 0.51562 | NA | NA | 20.8 | 0.011128 | NA | NA | 0.99 | 0.65715
31 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7113 | 23.3748 | 30.75 | 0.011128 | 1.25 | 22.6 | 0.011128 | 0.51562 | NA | NA | 22.6 | 0.011128 | NA | NA | 0.81 | 0.53827
32 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.9374 | 23.9816 | 40.25 | 0.019028 | 1.25 | 32.6 | 0.019028 | 0.29688 | NA | NA | 32.6 | 0.019028 | NA | NA | 0.63 | 0.4723
33 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
34 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.6379 | 36.5943 | 40.25 | 0.0093704 | 0.75 | 22.4 | 0.0093704 | 0.17812 | NA | NA | 22.4 | 0.0093704 | NA | NA | 0.99 | 0.65499
35 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7541 | 36.9061 | 40.25 | 0.019028 | 1.25 | 29.4 | 0.019028 | 0.29688 | NA | NA | 29.4 | 0.019028 | NA | NA | 0.89 | 0.66987
36 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.4314 | 27.9902 | 26 | 0.0062836 | 1 | 17.2 | 0.0062836 | 0.325 | NA | NA | 17.2 | 0.0062836 | NA | NA | 0.81 | 0.46574
37 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
38 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.6989 | 23.3415 | 30.75 | 0.0055148 | 1.25 | 21.3 | 0.0055148 | 0.29688 | NA | NA | 21.3 | 0.0055148 | NA | NA | 0.65 | 0.37036
39 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.6916 | 23.3219 | 30.75 | 0.0055148 | 0.75 | 20.7 | 0.0055148 | 0.17812 | NA | NA | 20.7 | 0.0055148 | NA | NA | 0.69 | 0.39388
40 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.875 | 23.8141 | 40.25 | 0.0093704 | 0.75 | 26.6 | 0.0093704 | 0.17812 | NA | NA | 26.6 | 0.0093704 | NA | NA | 0.76 | 0.50087
41 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.6881 | 36.7289 | 40.25 | 0.0093704 | 1.25 | 25.1 | 0.0093704 | 0.29688 | NA | NA | 25.1 | 0.0093704 | NA | NA | 0.84 | 0.55591
42 | N | 1 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6418 | 28.5549 | 35.5 | 0.010892 | 1 | 22.2 | 0.010892 | 0.325 | NA | NA | 22.2 | 0.010892 | NA | NA | 0.98 | 0.65777
43 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.3759 | 35.8913 | 30.75 | 0.0055148 | 0.75 | 17.7 | 0.0055148 | 0.17812 | NA | NA | 17.7 | 0.0055148 | NA | NA | 0.9 | 0.51145
44 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.9115 | 23.912 | 40.25 | 0.019028 | 0.75 | 30.4 | 0.019028 | 0.17812 | NA | NA | 30.4 | 0.019028 | NA | NA | 0.81 | 0.60813
45 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.2985 | 35.6836 | 30.75 | 0.0055148 | 0.75 | 13.6 | 0.0055148 | 0.30937 | NA | NA | 13.6 | 0.0055148 | NA | NA | 1.17 | 0.67214
46 | N | 0.5 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6958 | 28.6999 | 35.5 | 0.010892 | 1 | 25.9 | 0.010892 | 0.325 | NA | NA | 25.9 | 0.010892 | NA | NA | 0.7 | 0.47478
47 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
48 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7294 | 23.4233 | 30.75 | 0.011128 | 1.25 | 24.1 | 0.011128 | 0.51562 | NA | NA | 24.1 | 0.011128 | NA | NA | 0.66 | 0.4392
49 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.5 | 2.81 | 2.81 | 10.6462 | 28.5667 | 35.5 | 0.010892 | 1 | 22.5 | 0.010892 | 0.5 | NA | NA | 22.5 | 0.010892 | NA | NA | 0.96 | 0.64293
50 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.6714 | 36.684 | 40.25 | 0.0093704 | 0.75 | 24.2 | 0.0093704 | 0.17812 | NA | NA | 24.2 | 0.0093704 | NA | NA | 0.89 | 0.58894
51 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.435 | 36.0497 | 30.75 | 0.011128 | 0.75 | 21.1 | 0.011128 | 0.17812 | NA | NA | 21.1 | 0.011128 | NA | NA | 0.96 | 0.63734
52 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.3382 | 35.79 | 30.75 | 0.0055148 | 0.75 | 15.7 | 0.0055148 | 0.30937 | NA | NA | 15.7 | 0.0055148 | NA | NA | 1.03 | 0.58983
53 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6355 | 23.1714 | 30.75 | 0.0055148 | 0.75 | 16.1 | 0.0055148 | 0.30937 | NA | NA | 16.1 | 0.0055148 | NA | NA | 1 | 0.57416
54 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8161 | 23.6561 | 40.25 | 0.0093704 | 0.75 | 21.7 | 0.0093704 | 0.30937 | NA | NA | 21.7 | 0.0093704 | NA | NA | 1.03 | 0.68067
55 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
56 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6958 | 28.6999 | 35.5 | 0.010892 | 1.5 | 25.9 | 0.010892 | 0.4875 | NA | NA | 25.9 | 0.010892 | NA | NA | 0.7 | 0.47478
57 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4117 | 35.9874 | 30.75 | 0.0055148 | 1.25 | 19.6 | 0.0055148 | 0.29688 | NA | NA | 19.6 | 0.0055148 | NA | NA | 0.77 | 0.43699
58 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8761 | 23.8171 | 40.25 | 0.019028 | 0.75 | 27.4 | 0.019028 | 0.30937 | NA | NA | 27.4 | 0.019028 | NA | NA | 1.05 | 0.79335
59 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8954 | 23.8688 | 40.25 | 0.0093704 | 1.25 | 28.3 | 0.0093704 | 0.51562 | NA | NA | 28.3 | 0.0093704 | NA | NA | 0.66 | 0.43849
60 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.8885 | 29.2169 | 45 | 0.018279 | 1 | 30.3 | 0.018279 | 0.325 | NA | NA | 30.3 | 0.018279 | NA | NA | 0.9 | 0.68074
61 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.3571 | 35.8407 | 30.75 | 0.0055148 | 1.25 | 16.7 | 0.0055148 | 0.51562 | NA | NA | 16.7 | 0.0055148 | NA | NA | 0.96 | 0.55064
62 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4611 | 36.1197 | 30.75 | 0.011128 | 1.25 | 22.5 | 0.011128 | 0.29688 | NA | NA | 22.5 | 0.011128 | NA | NA | 0.82 | 0.54488
63 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6095 | 28.4682 | 35.5 | 0.0035887 | 1 | 19.6 | 0.0035887 | 0.325 | NA | NA | 19.6 | 0.0035887 | NA | NA | 0.83 | 0.43974
64 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6623 | 23.2434 | 30.75 | 0.0055148 | 0.75 | 18.3 | 0.0055148 | 0.30937 | NA | NA | 18.3 | 0.0055148 | NA | NA | 0.85 | 0.48794
65 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4536 | 36.0997 | 30.75 | 0.011128 | 0.75 | 22.1 | 0.011128 | 0.17812 | NA | NA | 22.1 | 0.011128 | NA | NA | 0.86 | 0.5713
66 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7017 | 23.3489 | 30.75 | 0.011128 | 0.75 | 21.8 | 0.011128 | 0.30937 | NA | NA | 21.8 | 0.011128 | NA | NA | 0.88 | 0.59111
67 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
68 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4163 | 35.9996 | 30.75 | 0.011128 | 0.75 | 20.1 | 0.011128 | 0.30937 | NA | NA | 20.1 | 0.011128 | NA | NA | 1.06 | 0.70339
69 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8962 | 23.8709 | 40.25 | 0.019028 | 0.75 | 29.1 | 0.019028 | 0.30937 | NA | NA | 29.1 | 0.019028 | NA | NA | 0.91 | 0.68839
70 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4816 | 36.1747 | 30.75 | 0.011128 | 1.25 | 23.6 | 0.011128 | 0.29688 | NA | NA | 23.6 | 0.011128 | NA | NA | 0.71 | 0.47223
71 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.7596 | 36.9207 | 40.25 | 0.019028 | 1.25 | 29.7 | 0.019028 | 0.51562 | NA | NA | 29.7 | 0.019028 | NA | NA | 0.87 | 0.65135
72 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8642 | 23.7851 | 40.25 | 0.0093704 | 1.25 | 25.7 | 0.0093704 | 0.51562 | NA | NA | 25.7 | 0.0093704 | NA | NA | 0.81 | 0.5339
73 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.9068 | 23.8994 | 40.25 | 0.019028 | 1.25 | 30 | 0.019028 | 0.51562 | NA | NA | 30 | 0.019028 | NA | NA | 0.84 | 0.63282
74 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.895 | 23.8677 | 40.25 | 0.019028 | 0.75 | 29 | 0.019028 | 0.17812 | NA | NA | 29 | 0.019028 | NA | NA | 0.92 | 0.69456
75 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6156 | 36.5344 | 40.25 | 0.0093704 | 0.75 | 21.2 | 0.0093704 | 0.30937 | NA | NA | 21.2 | 0.0093704 | NA | NA | 1.05 | 0.69902
76 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
77 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7171 | 23.3905 | 30.75 | 0.0055148 | 1.25 | 22.8 | 0.0055148 | 0.29688 | NA | NA | 22.8 | 0.0055148 | NA | NA | 0.54 | 0.31157
78 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.739 | 23.4492 | 30.75 | 0.011128 | 1.25 | 24.9 | 0.011128 | 0.29688 | NA | NA | 24.9 | 0.011128 | NA | NA | 0.58 | 0.38637
79 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6155 | 28.4843 | 35.5 | 0.010892 | 0.5 | 20.4 | 0.010892 | 0.1625 | NA | NA | 20.4 | 0.010892 | NA | NA | 1.11 | 0.74679
80 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.911 | 23.9106 | 40.25 | 0.0093704 | 1.25 | 29.6 | 0.0093704 | 0.29688 | NA | NA | 29.6 | 0.0093704 | NA | NA | 0.59 | 0.39079
81 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
82 | N | 0.75 | 0.005 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 7.483 | 20.0789 | 35.5 | 0.010892 | 1 | 25.5 | 0.010892 | 0.325 | NA | NA | 25.5 | 0.010892 | NA | NA | 0.73 | 0.49456
83 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7013 | 23.348 | 30.75 | 0.0055148 | 1.25 | 21.5 | 0.0055148 | 0.51562 | NA | NA | 21.5 | 0.0055148 | NA | NA | 0.64 | 0.36252
84 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.7268 | 36.8327 | 40.25 | 0.019028 | 1.25 | 27.9 | 0.019028 | 0.51562 | NA | NA | 27.9 | 0.019028 | NA | NA | 1.01 | 0.76248
85 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
86 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.5728 | 36.4195 | 40.25 | 0.0093704 | 0.75 | 18.9 | 0.0093704 | 0.30937 | NA | NA | 18.9 | 0.0093704 | NA | NA | 1.18 | 0.78342
87 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7065 | 23.3619 | 30.75 | 0.011128 | 0.75 | 22.2 | 0.011128 | 0.17812 | NA | NA | 22.2 | 0.011128 | NA | NA | 0.84 | 0.56469
88 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6881 | 36.7289 | 40.25 | 0.0093704 | 1.25 | 25.1 | 0.0093704 | 0.51562 | NA | NA | 25.1 | 0.0093704 | NA | NA | 0.84 | 0.55591
89 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4381 | 36.0581 | 30.75 | 0.0055148 | 1.25 | 21 | 0.0055148 | 0.29688 | NA | NA | 21 | 0.0055148 | NA | NA | 0.67 | 0.38212
90 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6836 | 23.3003 | 30.75 | 0.011128 | 0.75 | 20.3 | 0.011128 | 0.30937 | NA | NA | 20.3 | 0.011128 | NA | NA | 1.03 | 0.69018
91 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
92 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
93 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7796 | 36.9745 | 40.25 | 0.019028 | 1.25 | 30.8 | 0.019028 | 0.29688 | NA | NA | 30.8 | 0.019028 | NA | NA | 0.77 | 0.58343
94 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.8498 | 23.7464 | 40.25 | 0.0093704 | 0.75 | 24.5 | 0.0093704 | 0.17812 | NA | NA | 24.5 | 0.0093704 | NA | NA | 0.87 | 0.57793
95 | N | 0.75 | 0.002 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 18.5951 | 49.8956 | 35.5 | 0.010892 | 1 | 21.1 | 0.010892 | 0.325 | NA | NA | 21.1 | 0.010892 | NA | NA | 1.06 | 0.71217
96 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6884 | 36.7298 | 40.25 | 0.019028 | 0.75 | 25.8 | 0.019028 | 0.30937 | NA | NA | 25.8 | 0.019028 | NA | NA | 1.19 | 0.89213
97 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7197 | 23.3975 | 30.75 | 0.011128 | 0.75 | 23.3 | 0.011128 | 0.17812 | NA | NA | 23.3 | 0.011128 | NA | NA | 0.74 | 0.49204
98 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.7106 | 28.7394 | 35.5 | 0.018367 | 1 | 27.4 | 0.018367 | 0.325 | NA | NA | 27.4 | 0.018367 | NA | NA | 0.9 | 0.67406
99 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4573 | 36.1097 | 30.75 | 0.011128 | 1.25 | 22.3 | 0.011128 | 0.51562 | NA | NA | 22.3 | 0.011128 | NA | NA | 0.84 | 0.55809
100 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4004 | 35.957 | 30.75 | 0.0055148 | 0.75 | 19 | 0.0055148 | 0.17812 | NA | NA | 19 | 0.0055148 | NA | NA | 0.81 | 0.4605
101 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.3902 | 35.9295 | 30.75 | 0.011128 | 0.75 | 18.7 | 0.011128 | 0.30937 | NA | NA | 18.7 | 0.011128 | NA | NA | 1.19 | 0.79585
102 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.15 | 2.81 | 2.81 | 10.7104 | 28.739 | 35.5 | 0.010892 | 1 | 26.9 | 0.010892 | 0.15 | NA | NA | 26.9 | 0.010892 | NA | NA | 0.63 | 0.42532
103 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.887 | 23.8463 | 40.25 | 0.0093704 | 1.25 | 27.6 | 0.0093704 | 0.29688 | NA | NA | 27.6 | 0.0093704 | NA | NA | 0.7 | 0.46418
104 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.9198 | 23.9342 | 40.25 | 0.019028 | 1.25 | 31.1 | 0.019028 | 0.29688 | NA | NA | 31.1 | 0.019028 | NA | NA | 0.75 | 0.56491
105 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6398 | 36.5993 | 40.25 | 0.0093704 | 1.25 | 22.5 | 0.0093704 | 0.51562 | NA | NA | 22.5 | 0.0093704 | NA | NA | 0.99 | 0.65132