## Characteritics
Paper information
Authors | Lin et al.
Title | Towards a thermodynamically favorable dew point evaporative cooler via optimization
Year | 2020
Data type | Experimental data, extracted from graphs
Description | Horizontal 20-channel counterflow D-IEC with a Polyethylene Terephthalate (PET) sheet between dry and wet channels. Thin sheet of absorbent material on the wet channel surface to circulate water through capillary action. Evaluation of the impact of the primary air temperature and velocity at the heat exchanger inlet and the recirculation ratio on the primary and secondary air outlet temperature. Outlet specific humidity of the secondary air computed by performing an energy balance on the evaporative cooler.
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Wet surface theory |  | counterflow |  | counterflow |  | parallel
Water recirculation | No
Wall material | PET sheet
Configuration | PCC
Geometry |  |  |  | Measurement uncertainties
Length | 0.6 | m |  | Temperature | 0.03 | K
Width | 0.15 | m |  | Humidity | 0.03 | K_wb
Height | 0.0684 | m |  | Air flow | 2 | %
Channel height | 0.003 | m
Wall thickness | 0.0004 | m
Number of channels | 20 | -
Operating conditions |  |  |  | Tests
Primary fluid velocity | 1.11-2 | m/s |  | A | Varying T_pd_i
Secondary fluid velocity | 0.37-1.59 | m/s |  | B | Varying v_pd_i
Secondary-to-Primary flow rate ratio | 0.22-0.9 | kg/kg |  | C | Varying S/P
Water supplied | 0 | kg/s

## Data
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | A | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 763.367 | 7.54 | 32.9149 | 32.9149 | 30 | 0.011 | 2 | 19 | 0.011 | 0.66 | NA | 0 | 19 | 0.011 | 27.3 | 0.02106 | 1.1358 | 0.75506
2 | A | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 756.4378 | 7.54 | 33.056 | 33.056 | 32.4711 | 0.011 | 2 | 19.6 | 0.011 | 0.66 | NA | 0 | 19.6 | 0.011 | 29 | 0.022882 | 1.1286 | 0.75578
3 | A | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 749.4821 | 7.54 | 33.1994 | 33.1994 | 35 | 0.011 | 2 | 20.2 | 0.011 | 0.66 | NA | 0 | 20.2 | 0.011 | 31.8 | 0.024319 | 1.1215 | 0.75632
4 | A | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 743.1194 | 7.54 | 33.3323 | 33.3323 | 37.5036 | 0.011 | 2 | 20.6 | 0.011 | 0.66 | NA | 0 | 20.6 | 0.011 | 33.7 | 0.026251 | 1.1278 | 0.7658
5 | A | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 737.0738 | 7.54 | 33.46 | 33.46 | 40 | 0.011 | 2 | 20.9 | 0.011 | 0.66 | NA | 0 | 20.9 | 0.011 | 35.7 | 0.028209 | 1.1375 | 0.77742
6 | B | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 418.0053 | 7.54 | 33.1215 | 33.1215 | 35 | 0.011 | 1.1099 | 18.5 | 0.011 | 0.36626 | NA | 0 | 18.5 | 0.011 | 32.1 | 0.025578 | 1.2503 | 0.84319
7 | B | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 498.185 | 7.54 | 33.1352 | 33.1352 | 35 | 0.011 | 1.3239 | 18.8 | 0.011 | 0.4369 | NA | 0 | 18.8 | 0.011 | 32.3 | 0.025252 | 1.2275 | 0.82786
8 | B | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 578.0527 | 7.54 | 33.1536 | 33.1536 | 35 | 0.011 | 1.538 | 19.2 | 0.011 | 0.50754 | NA | 0 | 19.2 | 0.011 | 32.1 | 0.025009 | 1.1972 | 0.80742
9 | B | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 651.6672 | 7.54 | 33.1811 | 33.1811 | 35 | 0.011 | 1.7369 | 19.8 | 0.011 | 0.57319 | NA | 0 | 19.8 | 0.011 | 32.1 | 0.024521 | 1.1518 | 0.77676
10 | B | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 733.334 | 7.54 | 33.204 | 33.204 | 35 | 0.011 | 1.9575 | 20.3 | 0.011 | 0.64597 | NA | 0 | 20.3 | 0.011 | 31.9 | 0.024197 | 1.1139 | 0.75121
11 | C | 0.6 | 0.003 | 0.5 | 1 | 0.22 | 742.4748 | 7.54 | 33.3458 | 33.3458 | 35 | 0.011 | 2 | 23.4 | 0.011 | 0.44786 | NA | 0 | 23.4 | 0.011 | 33.8 | 0.027932 | 0.87898 | 0.59279
12 | C | 0.6 | 0.003 | 0.5 | 1 | 0.33 | 749.9236 | 7.54 | 33.1902 | 33.1902 | 35 | 0.011 | 2 | 20 | 0.011 | 0.65328 | NA | 0 | 20 | 0.011 | 32.2 | 0.024318 | 1.1366 | 0.76654
13 | C | 0.6 | 0.003 | 0.5 | 1 | 0.4 | 752.5815 | 7.54 | 33.1352 | 33.1352 | 35 | 0.011 | 2 | 18.8 | 0.011 | 0.80279 | NA | 0 | 18.8 | 0.011 | 30.5 | 0.022548 | 1.2275 | 0.82786
14 | C | 0.6 | 0.003 | 0.5 | 1 | 0.5 | 755.4781 | 7.54 | 33.0756 | 33.0756 | 35 | 0.011 | 2 | 17.5 | 0.011 | 1.0009 | NA | 0 | 17.5 | 0.011 | 28.4 | 0.020678 | 1.3261 | 0.8943
15 | C | 0.6 | 0.003 | 0.5 | 1 | 0.6 | 757.494 | 7.54 | 33.0343 | 33.0343 | 35 | 0.011 | 2 | 16.6 | 0.011 | 1.1931 | NA | 0 | 16.6 | 0.011 | 26 | 0.019555 | 1.3942 | 0.94029
16 | C | 0.6 | 0.003 | 0.5 | 1 | 0.7 | 758.3928 | 7.54 | 33.016 | 33.016 | 35 | 0.011 | 2 | 16.2 | 0.011 | 1.3957 | NA | 0 | 16.2 | 0.011 | 24.1 | 0.018636 | 1.4246 | 0.96073
17 | C | 0.6 | 0.003 | 0.5 | 1 | 0.9 | 759.068 | 7.54 | 33.0022 | 33.0022 | 35 | 0.011 | 2 | 15.9 | 0.011 | 1.5894 | NA | 0 | 15.9 | 0.011 | 23.6 | 0.016449 | 1.4473 | 0.97606