## Characteristics
Paper information
Authors | Pacak et al.
Title | Performance Analysis of the Multi-Stage Dew-Point Indirect Evaporative Air Cooler
Year | 2022
Data type | Numerical, extracted from graphs
Description | Numerical model of a hybrid IEC consisting of a D-IEC pre-cooled with a crossflow IEC module, based on the work of Anisimov et al. (2015). Model validation for the D-IEC configuration, using two sources of experimental results from the literature. The temperature profile of the primary air validated against the experimental results from Hsu et al. (1989). Comparison of predicted outlet temperature of primary air to the measured temperature reported by Lee et al. (2013) under various inlet conditions. Use of numerical model to predict the primary air outlet temperature when varying the secondary-to-primary air flow rate ratios and the relative length of both sections of the evaporative cooler.
EC characteristics |  |  | Configuration
EC type | 2-stage IEC |  | pd | sw_1 | pd | sw_2
EC 1 | IEC |  | Crossflow |  | Counterflow
EC 2 | D-IEC
Water injection type | Wet surface
Water recirculation | Yes
Wall material | NA
Configuration | XF/CF
Geometry
Length | 1 | m
Width | 1 | m
Height | 0.55 | m
Channel height | 0.003 | m
Wall thickness | 0.0005 | m
Number of channels | 185 | -
Operating conditions
Primary fluid velocity | 3 | m/s
Secondary fluid velocity | 0.3-3 | m/s
Secondary-to-Primary flow rate ratio | 0.1-1 | kg/kg
Water supplied | NA | kg/s

## Data
| Testing conditions | [12 empty] | Inlet conditions | [10 empty] | Outlet conditions
Run | Test | L_1 | L_2 | h_ch | W | WWR | SPR_1 | SPR_2 | Re | Nu | h_T_pd | h_T_sw_1 | h_T_sw_2 | T_pdi | w_pdi | v_pdi | T_swi_1 | w_swi_1 | v_swi_1 | T_swi_2 | w_swi_2 | v_swi_2 | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo_1 | w_wso_1 | T_swo_2 | w_wso_2 | epsilon_wb | epsilon_dp
1 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.8476 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 23.7882 | 0.012 | 0.3 | NA | NA | 23.7882 | 0.012 | NA | NA | NA | NA | 0.69311 | 0.46936
2 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.7561 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 22.7931 | 0.012 | 0.3 | NA | NA | 22.7931 | 0.012 | NA | NA | NA | NA | 0.80472 | 0.54494
3 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.7099 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 22.2906 | 0.012 | 0.3 | NA | NA | 22.2906 | 0.012 | NA | NA | NA | NA | 0.86052 | 0.58273
4 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6832 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 22 | 0.012 | 0.3 | NA | NA | 22 | 0.012 | NA | NA | NA | NA | 0.89289 | 0.60465
5 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.66 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.7488 | 0.012 | 0.3 | NA | NA | 21.7488 | 0.012 | NA | NA | NA | NA | 0.92079 | 0.62355
6 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6446 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.5813 | 0.012 | 0.3 | NA | NA | 21.5813 | 0.012 | NA | NA | NA | NA | 0.93977 | 0.6364
7 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6451 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.5862 | 0.012 | 0.3 | NA | NA | 21.5862 | 0.012 | NA | NA | NA | NA | 0.93865 | 0.63564
8 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6455 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.5911 | 0.012 | 0.3 | NA | NA | 21.5911 | 0.012 | NA | NA | NA | NA | 0.93865 | 0.63564
9 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.665 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.803 | 0.012 | 0.3 | NA | NA | 21.803 | 0.012 | NA | NA | NA | NA | 0.91521 | 0.61977
10 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.8295 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 23.5911 | 0.012 | 0.3 | NA | NA | 23.5911 | 0.012 | NA | NA | NA | NA | 0.71543 | 0.48448
11 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.738 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 22.5961 | 0.012 | 0.3 | NA | NA | 22.5961 | 0.012 | NA | NA | NA | NA | 0.82592 | 0.5593
12 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6732 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 21.8916 | 0.012 | 0.3 | NA | NA | 21.8916 | 0.012 | NA | NA | NA | NA | 0.90517 | 0.61297
13 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6365 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 21.4926 | 0.012 | 0.3 | NA | NA | 21.4926 | 0.012 | NA | NA | NA | NA | 0.94981 | 0.6432
14 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6097 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 21.202 | 0.012 | 0.3 | NA | NA | 21.202 | 0.012 | NA | NA | NA | NA | 0.98218 | 0.66512
15 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5952 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 21.0443 | 0.012 | 0.3 | NA | NA | 21.0443 | 0.012 | NA | NA | NA | NA | 1 | 0.67721
16 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5815 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 20.8966 | 0.012 | 0.3 | NA | NA | 20.8966 | 0.012 | NA | NA | NA | NA | 1.0157 | 0.68779
17 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.582 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 20.9015 | 0.012 | 0.3 | NA | NA | 20.9015 | 0.012 | NA | NA | NA | NA | 1.0157 | 0.68779
18 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.5 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5911 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 21 | 0.012 | 0.3 | NA | NA | 21 | 0.012 | NA | NA | NA | NA | 1.0045 | 0.68023
19 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.8204 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 23.4926 | 0.012 | 0.3 | NA | NA | 23.4926 | 0.012 | NA | NA | NA | NA | 0.72659 | 0.49204
20 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.7199 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 22.399 | 0.012 | 0.3 | NA | NA | 22.399 | 0.012 | NA | NA | NA | NA | 0.84824 | 0.57442
21 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.656 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 21.7044 | 0.012 | 0.3 | NA | NA | 21.7044 | 0.012 | NA | NA | NA | NA | 0.92637 | 0.62733
22 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6129 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 21.2365 | 0.012 | 0.3 | NA | NA | 21.2365 | 0.012 | NA | NA | NA | NA | 0.97771 | 0.66209
23 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5815 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.8966 | 0.012 | 0.3 | NA | NA | 20.8966 | 0.012 | NA | NA | NA | NA | 1.0157 | 0.68779
24 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5679 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.7488 | 0.012 | 0.3 | NA | NA | 20.7488 | 0.012 | NA | NA | NA | NA | 1.0324 | 0.69913
25 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5634 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.6995 | 0.012 | 0.3 | NA | NA | 20.6995 | 0.012 | NA | NA | NA | NA | 1.038 | 0.70291
26 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5543 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.601 | 0.012 | 0.3 | NA | NA | 20.601 | 0.012 | NA | NA | NA | NA | 1.0491 | 0.71047
27 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.7 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5675 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.7438 | 0.012 | 0.3 | NA | NA | 20.7438 | 0.012 | NA | NA | NA | NA | 1.0335 | 0.69989
28 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.8091 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 23.3695 | 0.012 | 0.3 | NA | NA | 23.3695 | 0.012 | NA | NA | NA | NA | 0.73998 | 0.50111
29 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.7045 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 22.2315 | 0.012 | 0.3 | NA | NA | 22.2315 | 0.012 | NA | NA | NA | NA | 0.86722 | 0.58727
30 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6437 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 21.5714 | 0.012 | 0.3 | NA | NA | 21.5714 | 0.012 | NA | NA | NA | NA | 0.94088 | 0.63715
31 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5979 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 21.0739 | 0.012 | 0.3 | NA | NA | 21.0739 | 0.012 | NA | NA | NA | NA | 0.99669 | 0.67494
32 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5661 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.7291 | 0.012 | 0.3 | NA | NA | 20.7291 | 0.012 | NA | NA | NA | NA | 1.0346 | 0.70064
33 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5516 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.5714 | 0.012 | 0.3 | NA | NA | 20.5714 | 0.012 | NA | NA | NA | NA | 1.0525 | 0.71273
34 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5339 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.3793 | 0.012 | 0.3 | NA | NA | 20.3793 | 0.012 | NA | NA | NA | NA | 1.0737 | 0.72709
35 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5339 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.3793 | 0.012 | 0.3 | NA | NA | 20.3793 | 0.012 | NA | NA | NA | NA | 1.0737 | 0.72709
36 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 0.1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5516 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.5714 | 0.012 | 0.3 | NA | NA | 20.5714 | 0.012 | NA | NA | NA | NA | 1.0525 | 0.71273
37 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4244 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.1927 | 0.012 | 0.9 | NA | NA | 19.1927 | 0.012 | NA | NA | NA | NA | 1.2065 | 0.81704
38 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4135 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.0754 | 0.012 | 0.9 | NA | NA | 19.0754 | 0.012 | NA | NA | NA | NA | 1.2188 | 0.82535
39 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4161 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.1034 | 0.012 | 0.9 | NA | NA | 19.1034 | 0.012 | NA | NA | NA | NA | 1.2166 | 0.82384
40 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4233 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.1816 | 0.012 | 0.9 | NA | NA | 19.1816 | 0.012 | NA | NA | NA | NA | 1.2076 | 0.81779
41 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4373 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.3324 | 0.012 | 0.9 | NA | NA | 19.3324 | 0.012 | NA | NA | NA | NA | 1.1909 | 0.80646
42 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4605 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.5838 | 0.012 | 0.9 | NA | NA | 19.5838 | 0.012 | NA | NA | NA | NA | 1.163 | 0.78756
43 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4981 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.9916 | 0.012 | 0.9 | NA | NA | 19.9916 | 0.012 | NA | NA | NA | NA | 1.1172 | 0.75657
44 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5491 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 20.5447 | 0.012 | 0.9 | NA | NA | 20.5447 | 0.012 | NA | NA | NA | NA | 1.0558 | 0.715
45 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6238 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.3547 | 0.012 | 0.9 | NA | NA | 21.3547 | 0.012 | NA | NA | NA | NA | 0.96544 | 0.65378
46 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4208 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.1536 | 0.012 | 0.9 | NA | NA | 19.1536 | 0.012 | NA | NA | NA | NA | 1.211 | 0.82006
47 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4048 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.9804 | 0.012 | 0.9 | NA | NA | 18.9804 | 0.012 | NA | NA | NA | NA | 1.23 | 0.83291
48 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4001 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.9302 | 0.012 | 0.9 | NA | NA | 18.9302 | 0.012 | NA | NA | NA | NA | 1.2355 | 0.83669
49 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4001 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.9302 | 0.012 | 0.9 | NA | NA | 18.9302 | 0.012 | NA | NA | NA | NA | 1.2355 | 0.83669
50 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4141 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.081 | 0.012 | 0.9 | NA | NA | 19.081 | 0.012 | NA | NA | NA | NA | 1.2188 | 0.82535
51 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4306 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.2598 | 0.012 | 0.9 | NA | NA | 19.2598 | 0.012 | NA | NA | NA | NA | 1.1987 | 0.81175
52 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4563 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.5391 | 0.012 | 0.9 | NA | NA | 19.5391 | 0.012 | NA | NA | NA | NA | 1.1675 | 0.79058
53 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4981 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.9916 | 0.012 | 0.9 | NA | NA | 19.9916 | 0.012 | NA | NA | NA | NA | 1.1172 | 0.75657
54 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.5 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5682 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 20.7514 | 0.012 | 0.9 | NA | NA | 20.7514 | 0.012 | NA | NA | NA | NA | 1.0324 | 0.69913
55 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4171 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 19.1145 | 0.012 | 0.9 | NA | NA | 19.1145 | 0.012 | NA | NA | NA | NA | 1.2154 | 0.82308
56 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4012 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.9413 | 0.012 | 0.9 | NA | NA | 18.9413 | 0.012 | NA | NA | NA | NA | 1.2344 | 0.83593
57 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3939 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.8631 | 0.012 | 0.9 | NA | NA | 18.8631 | 0.012 | NA | NA | NA | NA | 1.2433 | 0.84198
58 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3908 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.8296 | 0.012 | 0.9 | NA | NA | 18.8296 | 0.012 | NA | NA | NA | NA | 1.2467 | 0.84425
59 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4012 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.9413 | 0.012 | 0.9 | NA | NA | 18.9413 | 0.012 | NA | NA | NA | NA | 1.2344 | 0.83593
60 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4192 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 19.1369 | 0.012 | 0.9 | NA | NA | 19.1369 | 0.012 | NA | NA | NA | NA | 1.2121 | 0.82082
61 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4419 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 19.3827 | 0.012 | 0.9 | NA | NA | 19.3827 | 0.012 | NA | NA | NA | NA | 1.1853 | 0.80268
62 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4795 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 19.7905 | 0.012 | 0.9 | NA | NA | 19.7905 | 0.012 | NA | NA | NA | NA | 1.1395 | 0.77169
63 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.7 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5357 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.3994 | 0.012 | 0.9 | NA | NA | 20.3994 | 0.012 | NA | NA | NA | NA | 1.0715 | 0.72558
64 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.413 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 19.0698 | 0.012 | 0.9 | NA | NA | 19.0698 | 0.012 | NA | NA | NA | NA | 1.2199 | 0.82611
65 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3939 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.8631 | 0.012 | 0.9 | NA | NA | 18.8631 | 0.012 | NA | NA | NA | NA | 1.2433 | 0.84198
66 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3857 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.7737 | 0.012 | 0.9 | NA | NA | 18.7737 | 0.012 | NA | NA | NA | NA | 1.2534 | 0.84878
67 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3826 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.7402 | 0.012 | 0.9 | NA | NA | 18.7402 | 0.012 | NA | NA | NA | NA | 1.2567 | 0.85105
68 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3903 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.824 | 0.012 | 0.9 | NA | NA | 18.824 | 0.012 | NA | NA | NA | NA | 1.2478 | 0.845
69 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4037 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.9693 | 0.012 | 0.9 | NA | NA | 18.9693 | 0.012 | NA | NA | NA | NA | 1.2311 | 0.83366
70 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4269 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 19.2207 | 0.012 | 0.9 | NA | NA | 19.2207 | 0.012 | NA | NA | NA | NA | 1.2032 | 0.81477
71 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.46 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 19.5782 | 0.012 | 0.9 | NA | NA | 19.5782 | 0.012 | NA | NA | NA | NA | 1.163 | 0.78756
72 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 0.3 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5156 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.1816 | 0.012 | 0.9 | NA | NA | 20.1816 | 0.012 | NA | NA | NA | NA | 1.096 | 0.74221
73 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.311 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 17.9653 | 0.012 | 3 | NA | NA | 17.9653 | 0.012 | NA | NA | NA | NA | 1.3427 | 0.90925
74 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3151 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 18.0099 | 0.012 | 3 | NA | NA | 18.0099 | 0.012 | NA | NA | NA | NA | 1.3382 | 0.90622
75 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3233 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 18.099 | 0.012 | 3 | NA | NA | 18.099 | 0.012 | NA | NA | NA | NA | 1.3282 | 0.89942
76 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3453 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 18.3366 | 0.012 | 3 | NA | NA | 18.3366 | 0.012 | NA | NA | NA | NA | 1.3014 | 0.88128
77 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3693 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 18.5965 | 0.012 | 3 | NA | NA | 18.5965 | 0.012 | NA | NA | NA | NA | 1.2724 | 0.86163
78 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4057 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 18.9901 | 0.012 | 3 | NA | NA | 18.9901 | 0.012 | NA | NA | NA | NA | 1.2288 | 0.83215
79 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.453 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 19.5025 | 0.012 | 3 | NA | NA | 19.5025 | 0.012 | NA | NA | NA | NA | 1.1719 | 0.79361
80 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5174 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 20.2005 | 0.012 | 3 | NA | NA | 20.2005 | 0.012 | NA | NA | NA | NA | 1.0938 | 0.7407
81 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.6139 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | 21.2475 | 0.012 | 3 | NA | NA | 21.2475 | 0.012 | NA | NA | NA | NA | 0.9766 | 0.66134
82 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3068 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 17.9208 | 0.012 | 3 | NA | NA | 17.9208 | 0.012 | NA | NA | NA | NA | 1.3483 | 0.91303
83 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3103 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 17.9579 | 0.012 | 3 | NA | NA | 17.9579 | 0.012 | NA | NA | NA | NA | 1.3438 | 0.91
84 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3199 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.0619 | 0.012 | 3 | NA | NA | 18.0619 | 0.012 | NA | NA | NA | NA | 1.3326 | 0.90244
85 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3315 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.1881 | 0.012 | 3 | NA | NA | 18.1881 | 0.012 | NA | NA | NA | NA | 1.3181 | 0.89262
86 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3446 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.3292 | 0.012 | 3 | NA | NA | 18.3292 | 0.012 | NA | NA | NA | NA | 1.3025 | 0.88204
87 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3789 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 18.7005 | 0.012 | 3 | NA | NA | 18.7005 | 0.012 | NA | NA | NA | NA | 1.2612 | 0.85407
88 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4207 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.1535 | 0.012 | 3 | NA | NA | 19.1535 | 0.012 | NA | NA | NA | NA | 1.211 | 0.82006
89 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4708 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 19.6955 | 0.012 | 3 | NA | NA | 19.6955 | 0.012 | NA | NA | NA | NA | 1.1496 | 0.77849
90 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.5 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5639 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | 20.7054 | 0.012 | 3 | NA | NA | 20.7054 | 0.012 | NA | NA | NA | NA | 1.0369 | 0.70215
91 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3027 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 17.8762 | 0.012 | 3 | NA | NA | 17.8762 | 0.012 | NA | NA | NA | NA | 1.3527 | 0.91605
92 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3048 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 17.8985 | 0.012 | 3 | NA | NA | 17.8985 | 0.012 | NA | NA | NA | NA | 1.3505 | 0.91454
93 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3096 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 17.9505 | 0.012 | 3 | NA | NA | 17.9505 | 0.012 | NA | NA | NA | NA | 1.3449 | 0.91076
94 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3267 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.1361 | 0.012 | 3 | NA | NA | 18.1361 | 0.012 | NA | NA | NA | NA | 1.3237 | 0.8964
95 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3535 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.4257 | 0.012 | 3 | NA | NA | 18.4257 | 0.012 | NA | NA | NA | NA | 1.2913 | 0.87448
96 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.37 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 18.604 | 0.012 | 3 | NA | NA | 18.604 | 0.012 | NA | NA | NA | NA | 1.2724 | 0.86163
97 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.407 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 19.005 | 0.012 | 3 | NA | NA | 19.005 | 0.012 | NA | NA | NA | NA | 1.2277 | 0.8314
98 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4578 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 19.5545 | 0.012 | 3 | NA | NA | 19.5545 | 0.012 | NA | NA | NA | NA | 1.1663 | 0.78983
99 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.7 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5263 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | 20.297 | 0.012 | 3 | NA | NA | 20.297 | 0.012 | NA | NA | NA | NA | 1.0826 | 0.73314
100 | N | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.2979 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 17.8243 | 0.012 | 3 | NA | NA | 17.8243 | 0.012 | NA | NA | NA | NA | 1.3594 | 0.92058
101 | N | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.2972 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 17.8168 | 0.012 | 3 | NA | NA | 17.8168 | 0.012 | NA | NA | NA | NA | 1.3594 | 0.92058
102 | N | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3034 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 17.8837 | 0.012 | 3 | NA | NA | 17.8837 | 0.012 | NA | NA | NA | NA | 1.3527 | 0.91605
103 | N | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3164 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.0248 | 0.012 | 3 | NA | NA | 18.0248 | 0.012 | NA | NA | NA | NA | 1.3371 | 0.90547
104 | N | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3364 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.2401 | 0.012 | 3 | NA | NA | 18.2401 | 0.012 | NA | NA | NA | NA | 1.3125 | 0.88884
105 | N | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3597 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.4926 | 0.012 | 3 | NA | NA | 18.4926 | 0.012 | NA | NA | NA | NA | 1.2846 | 0.86994
106 | N | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.3913 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 18.8342 | 0.012 | 3 | NA | NA | 18.8342 | 0.012 | NA | NA | NA | NA | 1.2467 | 0.84425
107 | N | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.4379 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 19.3391 | 0.012 | 3 | NA | NA | 19.3391 | 0.012 | NA | NA | NA | NA | 1.1898 | 0.8057
108 | N | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 1 | 1107.3236 | 7.54 | 33.4161 | 33.4161 | 32.5057 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | 20.0743 | 0.012 | 3 | NA | NA | 20.0743 | 0.012 | NA | NA | NA | NA | 1.1083 | 0.75052