## Pacak2022
Paper information
Authors | Pacak et al.
Title | Performance Analysis of the Multi-Stage Dew-Point Indirect Evaporative Air Cooler
Year | 2022
Data type | Numerical, extracted from graphs
Description | Numerical model of a hybrid IEC consisting of a D-IEC pre-cooled with a crossflow IEC module, based on the work of Anisimov et al. (2015). Model validation for the D-IEC configuration, using two sources of experimental results from the literature. The temperature profile of the primary air validated against the experimental results from Hsu et al. (1989). Comparison of predicted outlet temperature of primary air to the measured temperature reported by Lee et al. (2013) under various inlet conditions. Use of numerical model to predict the primary air outlet temperature when varying the secondary-to-primary air flow rate ratios and the relative length of both sections of the evaporative cooler.
HEX characteristics |  |  | Configuration
HEX type | Hybrid IEC |  | pd | sw_x | pd | sw_c
Water injection type | Wet surface |  | Crossflow |  | Counterflow
Water recirculation | Yes
Wall material | NA
Configuration | CF/XF
Geometry
Length | 1 | m
Width | 1 | m
Height | 0.55 | m
Channel height | 0.003 | m
Wall thickness | 0.0005 | m
Number of channels | 185 | -
Operating conditions
Primary fluid velocity | 3 | m/s
Secondary fluid velocity | 0.3-3 | m/s
Secondary-to-Primary flow rate ratio | 0.1-1 | kg/kg
Water supplied | NA | kg/s
| Testing conditions | [10 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | L_x | L_c | h_ch | W | WWR | SPR_c | SPR_x | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi_x | w_swi_x | v_swi_x | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo_x | w_wso_x | T_swo_c | w_wso_c | epsilon_wb | epsilon_dp
1 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1127.6855 | 7.54 | 33.1324 | 33.1324 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 23.7882 | 0.012 | NA | NA | NA | NA | 0.69311 | 0.46936
2 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1131.0036 | 7.54 | 33.0868 | 33.0868 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 22.7931 | 0.012 | NA | NA | NA | NA | 0.80472 | 0.54494
3 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1132.685 | 7.54 | 33.0638 | 33.0638 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 22.2906 | 0.012 | NA | NA | NA | NA | 0.86052 | 0.58273
4 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1133.6595 | 7.54 | 33.0505 | 33.0505 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 22 | 0.012 | NA | NA | NA | NA | 0.89289 | 0.60465
5 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1134.5029 | 7.54 | 33.039 | 33.039 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.7488 | 0.012 | NA | NA | NA | NA | 0.92079 | 0.62355
6 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1135.0658 | 7.54 | 33.0313 | 33.0313 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.5813 | 0.012 | NA | NA | NA | NA | 0.93977 | 0.6364
7 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1135.0492 | 7.54 | 33.0315 | 33.0315 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.5862 | 0.012 | NA | NA | NA | NA | 0.93865 | 0.63564
8 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1135.0326 | 7.54 | 33.0318 | 33.0318 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.5911 | 0.012 | NA | NA | NA | NA | 0.93865 | 0.63564
9 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.1 | 0.3 | 1134.3209 | 7.54 | 33.0415 | 33.0415 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.803 | 0.012 | NA | NA | NA | NA | 0.91521 | 0.61977
10 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1128.3413 | 7.54 | 33.1234 | 33.1234 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 23.5911 | 0.012 | NA | NA | NA | NA | 0.71543 | 0.48448
11 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1131.6625 | 7.54 | 33.0778 | 33.0778 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 22.5961 | 0.012 | NA | NA | NA | NA | 0.82592 | 0.5593
12 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1134.0232 | 7.54 | 33.0455 | 33.0455 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 21.8916 | 0.012 | NA | NA | NA | NA | 0.90517 | 0.61297
13 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1135.3639 | 7.54 | 33.0273 | 33.0273 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 21.4926 | 0.012 | NA | NA | NA | NA | 0.94981 | 0.6432
14 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1136.3421 | 7.54 | 33.0139 | 33.0139 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 21.202 | 0.012 | NA | NA | NA | NA | 0.98218 | 0.66512
15 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1136.8732 | 7.54 | 33.0067 | 33.0067 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 21.0443 | 0.012 | NA | NA | NA | NA | 1 | 0.67721
16 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1137.3715 | 7.54 | 32.9999 | 32.9999 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 20.8966 | 0.012 | NA | NA | NA | NA | 1.0157 | 0.68779
17 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1137.3549 | 7.54 | 33.0002 | 33.0002 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 20.9015 | 0.012 | NA | NA | NA | NA | 1.0157 | 0.68779
18 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.1 | 0.5 | 1137.0227 | 7.54 | 33.0047 | 33.0047 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 21 | 0.012 | NA | NA | NA | NA | 1.0045 | 0.68023
19 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1128.6694 | 7.54 | 33.1188 | 33.1188 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 23.4926 | 0.012 | NA | NA | NA | NA | 0.72659 | 0.49204
20 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1132.322 | 7.54 | 33.0688 | 33.0688 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 22.399 | 0.012 | NA | NA | NA | NA | 0.84824 | 0.57442
21 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1134.6519 | 7.54 | 33.037 | 33.037 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 21.7044 | 0.012 | NA | NA | NA | NA | 0.92637 | 0.62733
22 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1136.226 | 7.54 | 33.0155 | 33.0155 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 21.2365 | 0.012 | NA | NA | NA | NA | 0.97771 | 0.66209
23 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1137.3715 | 7.54 | 32.9999 | 32.9999 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.8966 | 0.012 | NA | NA | NA | NA | 1.0157 | 0.68779
24 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1137.8701 | 7.54 | 32.9932 | 32.9932 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.7488 | 0.012 | NA | NA | NA | NA | 1.0324 | 0.69913
25 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1138.0364 | 7.54 | 32.9909 | 32.9909 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.6995 | 0.012 | NA | NA | NA | NA | 1.038 | 0.70291
26 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1138.3691 | 7.54 | 32.9864 | 32.9864 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.601 | 0.012 | NA | NA | NA | NA | 1.0491 | 0.71047
27 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.1 | 0.7 | 1137.8868 | 7.54 | 32.9929 | 32.9929 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.7438 | 0.012 | NA | NA | NA | NA | 1.0335 | 0.69989
28 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.1 | 1 | 1129.0798 | 7.54 | 33.1132 | 33.1132 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 23.3695 | 0.012 | NA | NA | NA | NA | 0.73998 | 0.50111
29 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.1 | 1 | 1132.8831 | 7.54 | 33.0611 | 33.0611 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 22.2315 | 0.012 | NA | NA | NA | NA | 0.86722 | 0.58727
30 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.1 | 1 | 1135.0989 | 7.54 | 33.0309 | 33.0309 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 21.5714 | 0.012 | NA | NA | NA | NA | 0.94088 | 0.63715
31 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.1 | 1 | 1136.7736 | 7.54 | 33.0081 | 33.0081 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 21.0739 | 0.012 | NA | NA | NA | NA | 0.99669 | 0.67494
32 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.1 | 1 | 1137.9367 | 7.54 | 32.9923 | 32.9923 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.7291 | 0.012 | NA | NA | NA | NA | 1.0346 | 0.70064
33 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.1 | 1 | 1138.469 | 7.54 | 32.985 | 32.985 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.5714 | 0.012 | NA | NA | NA | NA | 1.0525 | 0.71273
34 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.1 | 1 | 1139.1183 | 7.54 | 32.9762 | 32.9762 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.3793 | 0.012 | NA | NA | NA | NA | 1.0737 | 0.72709
35 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.1 | 1 | 1139.1183 | 7.54 | 32.9762 | 32.9762 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.3793 | 0.012 | NA | NA | NA | NA | 1.0737 | 0.72709
36 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.1 | 1 | 1138.469 | 7.54 | 32.985 | 32.985 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.5714 | 0.012 | NA | NA | NA | NA | 1.0525 | 0.71273
37 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1143.1419 | 7.54 | 32.9218 | 32.9218 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.1927 | 0.012 | NA | NA | NA | NA | 1.2065 | 0.81704
38 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1143.541 | 7.54 | 32.9164 | 32.9164 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.0754 | 0.012 | NA | NA | NA | NA | 1.2188 | 0.82535
39 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1143.4459 | 7.54 | 32.9177 | 32.9177 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.1034 | 0.012 | NA | NA | NA | NA | 1.2166 | 0.82384
40 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1143.1799 | 7.54 | 32.9213 | 32.9213 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.1816 | 0.012 | NA | NA | NA | NA | 1.2076 | 0.81779
41 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1142.6671 | 7.54 | 32.9282 | 32.9282 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.3324 | 0.012 | NA | NA | NA | NA | 1.1909 | 0.80646
42 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1141.8133 | 7.54 | 32.9397 | 32.9397 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.5838 | 0.012 | NA | NA | NA | NA | 1.163 | 0.78756
43 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1140.4304 | 7.54 | 32.9584 | 32.9584 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.9916 | 0.012 | NA | NA | NA | NA | 1.1172 | 0.75657
44 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1138.5593 | 7.54 | 32.9838 | 32.9838 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 20.5447 | 0.012 | NA | NA | NA | NA | 1.0558 | 0.715
45 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 0.3 | 1135.8277 | 7.54 | 33.0209 | 33.0209 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.3547 | 0.012 | NA | NA | NA | NA | 0.96544 | 0.65378
46 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1143.2749 | 7.54 | 32.92 | 32.92 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.1536 | 0.012 | NA | NA | NA | NA | 1.211 | 0.82006
47 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1143.8642 | 7.54 | 32.9121 | 32.9121 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.9804 | 0.012 | NA | NA | NA | NA | 1.23 | 0.83291
48 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1144.0354 | 7.54 | 32.9097 | 32.9097 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.9302 | 0.012 | NA | NA | NA | NA | 1.2355 | 0.83669
49 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1144.0354 | 7.54 | 32.9097 | 32.9097 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.9302 | 0.012 | NA | NA | NA | NA | 1.2355 | 0.83669
50 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1143.522 | 7.54 | 32.9167 | 32.9167 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.081 | 0.012 | NA | NA | NA | NA | 1.2188 | 0.82535
51 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1142.914 | 7.54 | 32.9249 | 32.9249 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.2598 | 0.012 | NA | NA | NA | NA | 1.1987 | 0.81175
52 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1141.965 | 7.54 | 32.9377 | 32.9377 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.5391 | 0.012 | NA | NA | NA | NA | 1.1675 | 0.79058
53 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1140.4304 | 7.54 | 32.9584 | 32.9584 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.9916 | 0.012 | NA | NA | NA | NA | 1.1172 | 0.75657
54 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 0.5 | 1137.8613 | 7.54 | 32.9933 | 32.9933 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 20.7514 | 0.012 | NA | NA | NA | NA | 1.0324 | 0.69913
55 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1143.4079 | 7.54 | 32.9182 | 32.9182 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 19.1145 | 0.012 | NA | NA | NA | NA | 1.2154 | 0.82308
56 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1143.9973 | 7.54 | 32.9103 | 32.9103 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.9413 | 0.012 | NA | NA | NA | NA | 1.2344 | 0.83593
57 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1144.2637 | 7.54 | 32.9067 | 32.9067 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.8631 | 0.012 | NA | NA | NA | NA | 1.2433 | 0.84198
58 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1144.3779 | 7.54 | 32.9051 | 32.9051 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.8296 | 0.012 | NA | NA | NA | NA | 1.2467 | 0.84425
59 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1143.9973 | 7.54 | 32.9103 | 32.9103 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.9413 | 0.012 | NA | NA | NA | NA | 1.2344 | 0.83593
60 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1143.3319 | 7.54 | 32.9192 | 32.9192 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 19.1369 | 0.012 | NA | NA | NA | NA | 1.2121 | 0.82082
61 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1142.4963 | 7.54 | 32.9305 | 32.9305 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 19.3827 | 0.012 | NA | NA | NA | NA | 1.1853 | 0.80268
62 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1141.112 | 7.54 | 32.9492 | 32.9492 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 19.7905 | 0.012 | NA | NA | NA | NA | 1.1395 | 0.77169
63 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 0.7 | 1139.0502 | 7.54 | 32.9771 | 32.9771 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.3994 | 0.012 | NA | NA | NA | NA | 1.0715 | 0.72558
64 | 0.1 | 0.9 | 0.003 | 1 | 1 | 0.3 | 1 | 1143.56 | 7.54 | 32.9162 | 32.9162 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 19.0698 | 0.012 | NA | NA | NA | NA | 1.2199 | 0.82611
65 | 0.2 | 0.8 | 0.003 | 1 | 1 | 0.3 | 1 | 1144.2637 | 7.54 | 32.9067 | 32.9067 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.8631 | 0.012 | NA | NA | NA | NA | 1.2433 | 0.84198
66 | 0.3 | 0.7 | 0.003 | 1 | 1 | 0.3 | 1 | 1144.5682 | 7.54 | 32.9026 | 32.9026 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.7737 | 0.012 | NA | NA | NA | NA | 1.2534 | 0.84878
67 | 0.4 | 0.6 | 0.003 | 1 | 1 | 0.3 | 1 | 1144.6824 | 7.54 | 32.901 | 32.901 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.7402 | 0.012 | NA | NA | NA | NA | 1.2567 | 0.85105
68 | 0.5 | 0.5 | 0.003 | 1 | 1 | 0.3 | 1 | 1144.3969 | 7.54 | 32.9049 | 32.9049 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.824 | 0.012 | NA | NA | NA | NA | 1.2478 | 0.845
69 | 0.6 | 0.4 | 0.003 | 1 | 1 | 0.3 | 1 | 1143.9022 | 7.54 | 32.9115 | 32.9115 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.9693 | 0.012 | NA | NA | NA | NA | 1.2311 | 0.83366
70 | 0.7 | 0.3 | 0.003 | 1 | 1 | 0.3 | 1 | 1143.0469 | 7.54 | 32.9231 | 32.9231 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 19.2207 | 0.012 | NA | NA | NA | NA | 1.2032 | 0.81477
71 | 0.8 | 0.2 | 0.003 | 1 | 1 | 0.3 | 1 | 1141.8323 | 7.54 | 32.9395 | 32.9395 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 19.5782 | 0.012 | NA | NA | NA | NA | 1.163 | 0.78756
72 | 0.9 | 0.1 | 0.003 | 1 | 1 | 0.3 | 1 | 1139.7872 | 7.54 | 32.9672 | 32.9672 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.1816 | 0.012 | NA | NA | NA | NA | 1.096 | 0.74221
73 | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 0.3 | 1147.3282 | 7.54 | 32.8655 | 32.8655 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 17.9653 | 0.012 | NA | NA | NA | NA | 1.3427 | 0.90925
74 | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 0.3 | 1147.1758 | 7.54 | 32.8675 | 32.8675 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 18.0099 | 0.012 | NA | NA | NA | NA | 1.3382 | 0.90622
75 | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 0.3 | 1146.8711 | 7.54 | 32.8716 | 32.8716 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 18.099 | 0.012 | NA | NA | NA | NA | 1.3282 | 0.89942
76 | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 0.3 | 1146.0592 | 7.54 | 32.8825 | 32.8825 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 18.3366 | 0.012 | NA | NA | NA | NA | 1.3014 | 0.88128
77 | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 0.3 | 1145.1723 | 7.54 | 32.8944 | 32.8944 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 18.5965 | 0.012 | NA | NA | NA | NA | 1.2724 | 0.86163
78 | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 0.3 | 1143.8313 | 7.54 | 32.9125 | 32.9125 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 18.9901 | 0.012 | NA | NA | NA | NA | 1.2288 | 0.83215
79 | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 0.3 | 1142.0894 | 7.54 | 32.936 | 32.936 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 19.5025 | 0.012 | NA | NA | NA | NA | 1.1719 | 0.79361
80 | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 0.3 | 1139.7232 | 7.54 | 32.968 | 32.968 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 20.2005 | 0.012 | NA | NA | NA | NA | 1.0938 | 0.7407
81 | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 0.3 | 1136.1887 | 7.54 | 33.016 | 33.016 | 30 | 0.012 | 3 | 30 | 0.012 | 0.9 | NA | NA | 21.2475 | 0.012 | NA | NA | NA | NA | 0.9766 | 0.66134
82 | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 0.5 | 1147.4806 | 7.54 | 32.8634 | 32.8634 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 17.9208 | 0.012 | NA | NA | NA | NA | 1.3483 | 0.91303
83 | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 0.5 | 1147.3536 | 7.54 | 32.8651 | 32.8651 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 17.9579 | 0.012 | NA | NA | NA | NA | 1.3438 | 0.91
84 | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 0.5 | 1146.998 | 7.54 | 32.8699 | 32.8699 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.0619 | 0.012 | NA | NA | NA | NA | 1.3326 | 0.90244
85 | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 0.5 | 1146.5665 | 7.54 | 32.8757 | 32.8757 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.1881 | 0.012 | NA | NA | NA | NA | 1.3181 | 0.89262
86 | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 0.5 | 1146.0846 | 7.54 | 32.8822 | 32.8822 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.3292 | 0.012 | NA | NA | NA | NA | 1.3025 | 0.88204
87 | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 0.5 | 1144.8178 | 7.54 | 32.8992 | 32.8992 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 18.7005 | 0.012 | NA | NA | NA | NA | 1.2612 | 0.85407
88 | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 0.5 | 1143.2755 | 7.54 | 32.92 | 32.92 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.1535 | 0.012 | NA | NA | NA | NA | 1.211 | 0.82006
89 | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 0.5 | 1141.4341 | 7.54 | 32.9449 | 32.9449 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 19.6955 | 0.012 | NA | NA | NA | NA | 1.1496 | 0.77849
90 | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 0.5 | 1138.0164 | 7.54 | 32.9912 | 32.9912 | 30 | 0.012 | 3 | 30 | 0.012 | 1.5 | NA | NA | 20.7054 | 0.012 | NA | NA | NA | NA | 1.0369 | 0.70215
91 | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 0.7 | 1147.6331 | 7.54 | 32.8614 | 32.8614 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 17.8762 | 0.012 | NA | NA | NA | NA | 1.3527 | 0.91605
92 | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 0.7 | 1147.5568 | 7.54 | 32.8624 | 32.8624 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 17.8985 | 0.012 | NA | NA | NA | NA | 1.3505 | 0.91454
93 | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 0.7 | 1147.379 | 7.54 | 32.8648 | 32.8648 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 17.9505 | 0.012 | NA | NA | NA | NA | 1.3449 | 0.91076
94 | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 0.7 | 1146.7442 | 7.54 | 32.8733 | 32.8733 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.1361 | 0.012 | NA | NA | NA | NA | 1.3237 | 0.8964
95 | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 0.7 | 1145.755 | 7.54 | 32.8866 | 32.8866 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.4257 | 0.012 | NA | NA | NA | NA | 1.2913 | 0.87448
96 | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 0.7 | 1145.147 | 7.54 | 32.8948 | 32.8948 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 18.604 | 0.012 | NA | NA | NA | NA | 1.2724 | 0.86163
97 | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 0.7 | 1143.7808 | 7.54 | 32.9132 | 32.9132 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 19.005 | 0.012 | NA | NA | NA | NA | 1.2277 | 0.8314
98 | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 0.7 | 1141.9129 | 7.54 | 32.9384 | 32.9384 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 19.5545 | 0.012 | NA | NA | NA | NA | 1.1663 | 0.78983
99 | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 0.7 | 1139.3966 | 7.54 | 32.9724 | 32.9724 | 30 | 0.012 | 3 | 30 | 0.012 | 2.1 | NA | NA | 20.297 | 0.012 | NA | NA | NA | NA | 1.0826 | 0.73314
100 | 0.1 | 0.9 | 0.003 | 1 | 1 | 1 | 1 | 1147.811 | 7.54 | 32.859 | 32.859 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 17.8243 | 0.012 | NA | NA | NA | NA | 1.3594 | 0.92058
101 | 0.2 | 0.8 | 0.003 | 1 | 1 | 1 | 1 | 1147.8364 | 7.54 | 32.8586 | 32.8586 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 17.8168 | 0.012 | NA | NA | NA | NA | 1.3594 | 0.92058
102 | 0.3 | 0.7 | 0.003 | 1 | 1 | 1 | 1 | 1147.6077 | 7.54 | 32.8617 | 32.8617 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 17.8837 | 0.012 | NA | NA | NA | NA | 1.3527 | 0.91605
103 | 0.4 | 0.6 | 0.003 | 1 | 1 | 1 | 1 | 1147.125 | 7.54 | 32.8682 | 32.8682 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.0248 | 0.012 | NA | NA | NA | NA | 1.3371 | 0.90547
104 | 0.5 | 0.5 | 0.003 | 1 | 1 | 1 | 1 | 1146.3889 | 7.54 | 32.8781 | 32.8781 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.2401 | 0.012 | NA | NA | NA | NA | 1.3125 | 0.88884
105 | 0.6 | 0.4 | 0.003 | 1 | 1 | 1 | 1 | 1145.5269 | 7.54 | 32.8897 | 32.8897 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.4926 | 0.012 | NA | NA | NA | NA | 1.2846 | 0.86994
106 | 0.7 | 0.3 | 0.003 | 1 | 1 | 1 | 1 | 1144.3624 | 7.54 | 32.9053 | 32.9053 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 18.8342 | 0.012 | NA | NA | NA | NA | 1.2467 | 0.84425
107 | 0.8 | 0.2 | 0.003 | 1 | 1 | 1 | 1 | 1142.6443 | 7.54 | 32.9285 | 32.9285 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 19.3391 | 0.012 | NA | NA | NA | NA | 1.1898 | 0.8057
108 | 0.9 | 0.1 | 0.003 | 1 | 1 | 1 | 1 | 1140.1505 | 7.54 | 32.96 | 32.9622 | 30 | 0.012 | 3 | 30 | 0.012 | 3 | NA | NA | 20.0743 | 0.012 | NA | NA | NA | NA | 1.1083 | 0.75052