## Kovacevic2017
Paper information
Authors | Kovacevic & Sourbron
Title | The numerical model for direct evaporative cooler
Year | 2017
Data type | Experimental and numerical, from tables
Description | Experimental testing of a finned DEC with water sprayed perpendicularly to the main airflow direction. 1. Comparison of experimental results and numerical simulation. 2. Use of numerical model to investigate the impact of the inlet conditions on the DEC performance. Air velocity determines the pad effectiveness, with lower velocities giving higher effectiveness, and vice versa. Relative humidity drastically influences the water evaporation rate while not impacting effectiveness. An increasing inlet air temperature slightly increases effectiveness and water consumption.
HEX characteristics |  |  | Configuration
HEX type | DEC |  | pd | wf
Water injection type | Wet surface |  | Crossflow
Water recirculation | Yes
Wall material | Aluminium
Configuration | PX
Geometry
Length | 0.09 | m
Width | NA | m
Height | NA | m
Channel height | 0.00416 | m
Wall thickness | 0.0007 | m
Number of channels | NA | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 1-3 | m/s |  | E | Experimental data
Water supplied | NA | kg/s |  | N | Numerical simulation
| Testing conditions | [7 empty] | Inlet conditions |  |  |  |  | Outlet conditions
Run | Test | L | h_ch | W | WWR | Re | Nu | h_T | T_pwi | w_pwi | v_pwi | T_wfi | m_dot_wf | T_pwo | w_pwo | epsilon_wb
1 | E | 0.09 | 0.00416 | NA | 1.141 | 420.5454 | 7.54 | 28.1767 | 48 | 0.0214 | 1 | NA | NA | 31.1 | 0.028327 | 0.98667
2 | E | 0.09 | 0.00416 | NA | 1.141 | 430.7641 | 7.54 | 27.9324 | 44 | 0.017333 | 1 | NA | NA | 28.1 | 0.023814 | 0.99181
3 | E | 0.09 | 0.00416 | NA | 1.141 | 440.8042 | 7.54 | 27.6895 | 40 | 0.013971 | 1 | NA | NA | 25.3 | 0.019936 | 0.98584
4 | E | 0.09 | 0.00416 | NA | 1.141 | 450.938 | 7.54 | 27.4415 | 36 | 0.011201 | 1 | NA | NA | 22.5 | 0.016662 | 0.98028
5 | E | 0.09 | 0.00416 | NA | 1.141 | 461.0633 | 7.54 | 27.1931 | 32 | 0.0089297 | 1 | NA | NA | 19.8 | 0.013852 | 0.96686
6 | E | 0.09 | 0.00416 | NA | 1.141 | 471.4821 | 7.54 | 26.9376 | 28 | 0.0070758 | 1 | NA | NA | 17 | 0.011507 | 0.95999
7 | E | 0.09 | 0.00416 | NA | 1.141 | 482.242 | 7.54 | 26.6754 | 24 | 0.0055707 | 1 | NA | NA | 14.1 | 0.0095559 | 0.961
8 | E | 0.09 | 0.00416 | NA | 1.141 | 493.3908 | 7.54 | 26.4068 | 20 | 0.0043558 | 1 | NA | NA | 11.1 | 0.0079377 | 0.97167
9 | E | 0.09 | 0.00416 | NA | 1.141 | 429.8865 | 7.54 | 27.8551 | 40 | 0.023638 | 1 | NA | NA | 30.5 | 0.027549 | 0.97999
10 | E | 0.09 | 0.00416 | NA | 1.141 | 441.2987 | 7.54 | 27.5952 | 36 | 0.018895 | 1 | NA | NA | 27.1 | 0.022536 | 0.98566
11 | E | 0.09 | 0.00416 | NA | 1.141 | 452.6478 | 7.54 | 27.3321 | 32 | 0.015027 | 1 | NA | NA | 23.8 | 0.018364 | 0.98243
12 | E | 0.09 | 0.00416 | NA | 1.141 | 463.967 | 7.54 | 27.0671 | 28 | 0.011883 | 1 | NA | NA | 20.6 | 0.014884 | 0.96756
13 | E | 0.09 | 0.00416 | NA | 1.141 | 475.5738 | 7.54 | 26.7937 | 24 | 0.0093403 | 1 | NA | NA | 17.3 | 0.01205 | 0.96565
14 | E | 0.09 | 0.00416 | NA | 1.141 | 487.3806 | 7.54 | 26.5166 | 20 | 0.0072937 | 1 | NA | NA | 14 | 0.0097169 | 0.96408
15 | E | 0.09 | 0.00416 | NA | 1.141 | 444.9445 | 7.54 | 27.4528 | 32 | 0.021243 | 1 | NA | NA | 27.4 | 0.023132 | 0.98353
16 | E | 0.09 | 0.00416 | NA | 1.141 | 457.1499 | 7.54 | 27.1791 | 28 | 0.016765 | 1 | NA | NA | 23.8 | 0.01848 | 0.97328
17 | E | 0.09 | 0.00416 | NA | 1.141 | 469.4539 | 7.54 | 26.8989 | 24 | 0.013155 | 1 | NA | NA | 20.2 | 0.0147 | 0.96371
18 | E | 0.09 | 0.00416 | NA | 1.141 | 481.9138 | 7.54 | 26.6136 | 20 | 0.010259 | 1 | NA | NA | 16.6 | 0.011638 | 0.95428
19 | N | 0.09 | 0.00416 | NA | 1.141 | 451.3786 | 7.54 | 27.3935 | 34 | 0.013417 | 1 | NA | NA | 23.35 | 0.0179 | 0.98192
20 | N | 0.09 | 0.00416 | NA | 1.141 | 900.8306 | 7.54 | 27.4209 | 34 | 0.013417 | 2 | NA | NA | 24.08 | 0.0177 | 0.91461
21 | N | 0.09 | 0.00416 | NA | 1.141 | 1348.2871 | 7.54 | 27.449 | 34 | 0.013417 | 3 | NA | NA | 24.83 | 0.0174 | 0.84546
22 | N | 0.09 | 0.00416 | NA | 1.141 | 948.4394 | 7.54 | 26.9331 | 30 | 0.0026293 | 2 | NA | NA | 14.72 | 0.0091 | 0.91024
23 | N | 0.09 | 0.00416 | NA | 1.141 | 922.77 | 7.54 | 27.1572 | 30 | 0.010652 | 2 | NA | NA | 20.93 | 0.0145 | 0.91226
24 | N | 0.09 | 0.00416 | NA | 1.141 | 901.3114 | 7.54 | 27.3276 | 30 | 0.018884 | 2 | NA | NA | 25.89 | 0.0207 | 0.91383
25 | N | 0.09 | 0.00416 | NA | 1.141 | 904.6947 | 7.54 | 27.4112 | 35 | 0.01059 | 2 | NA | NA | 22.66 | 0.0159 | 0.91514
26 | N | 0.09 | 0.00416 | NA | 1.141 | 957.4187 | 7.54 | 26.7628 | 25 | 0.0059177 | 2 | NA | NA | 15.39 | 0.01 | 0.90745
27 | N | 0.09 | 0.00416 | NA | 1.141 | 1013.3426 | 7.54 | 26.0938 | 15 | 0.00317 | 2 | NA | NA | 8.01 | 0.0061 | 0.89948