## Kashyap2020
Paper information
Authors | Kashyap et al.
Title | Comparative performance analysis of diﬀerent novel regenerative evaporative cooling device topologies
Year | 2020
Data type | Numerical data, extracted from graphs
Description | Development of a numerical D-IEC model that can be applied to various flow arrangements, validated using the experimental results of Riangvilaikul and Kumar (2010). Comparison of 8 D-IEC configurations: 4 parallel/counterflow and 4 crossflow configurations. Comparison of performance under varying operating conditions and geometric parameters. Effect of water temperature and flow rate, extraction ratio of primary air, gap size between channels, primary air velocity, and inlet wet bulb temperature.
HEX characteristics
HEX type | R-IEC
Water injection type | Wet surface theory
Water recirculation | No
Wall material | NA
Configuration | cfr. Test
Geometry
Length | 0.5 | m
Width | 0.5 | m
Height | 0.7 | m
Channel height | 0.005 | m
Wall thickness | 0.0005 | m
Number of channels | 140 | -
Operating conditions
Primary fluid velocity | 1-3.3 | m/s
Secondary fluid velocity | 0.3-1.4 | m/s
Secondary-to-Primary flow rate ratio | 0.3-0.7 | kg/kg
Water supplied | 0-0.0167 | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 55.3304 | 32.7138 | 35 | 0.0112 | 2 | 25.7949 | 0.0112 | 0.6 | 27 | 2.7778e-05 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.48069
2 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 55.3307 | 32.7146 | 35 | 0.0112 | 2 | 25.9867 | 0.0112 | 0.6 | 27 | 0.00025278 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.47032
3 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.1432 | 20.7572 | 55.3316 | 32.7176 | 35 | 0.0112 | 2 | 26.7538 | 0.0112 | 0.6 | 27 | 0.0013417 | 26.7538 | 0.0112 | NA | NA | 0.63433 | 0.43343
4 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 27 | 0.0027528 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40807
5 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 27 | 0.0055278 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.38559
6 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 27 | 0.008325 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.37579
7 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27 | 0.0111 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.37061
8 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27 | 0.013922 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.36715
9 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27 | 0.016694 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.36542
10 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 55.3304 | 32.7138 | 35 | 0.0112 | 2 | 25.7949 | 0.0112 | 0.6 | 25 | 4.1667e-05 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.48473
11 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.2552 | 20.7893 | 55.3302 | 32.7131 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.6 | 25 | 0.0003 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.4853
12 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 55.3304 | 32.7138 | 35 | 0.0112 | 2 | 25.7949 | 0.0112 | 0.6 | 25 | 0.0013528 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.47781
13 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 55.3307 | 32.7146 | 35 | 0.0112 | 2 | 25.9867 | 0.0112 | 0.6 | 25 | 0.0027667 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.46801
14 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 25 | 0.0055389 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45821
15 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.008325 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45303
16 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.011111 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45072
17 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.013886 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44841
18 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.016694 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44669
19 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.2552 | 20.7893 | 55.3302 | 32.7131 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.6 | 23 | 1.6667e-05 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.49337
20 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 23 | 0.00023889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.49798
21 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 23 | 0.0013528 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.5245
22 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.0027417 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52968
23 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.0055528 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.53026
24 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.0083361 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.53026
25 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.011111 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52968
26 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.013886 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52968
27 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.016669 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52911
28 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 21 | 1.6667e-05 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.49798
29 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 21 | 0.00023889 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.51239
30 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.7726 | 20.8322 | 55.3283 | 32.707 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 0.6 | 21 | 0.0013528 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.57061
31 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.1582 | 20.843 | 55.3278 | 32.7054 | 35 | 0.0112 | 2 | 23.6854 | 0.0112 | 0.6 | 21 | 0.0027278 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.59251
32 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.852 | 20.8483 | 55.3276 | 32.7047 | 35 | 0.0112 | 2 | 23.4936 | 0.0112 | 0.6 | 21 | 0.0055389 | 23.4936 | 0.0112 | NA | NA | 0.88511 | 0.60403
33 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.008325 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.60865
34 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.011111 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.61037
35 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.013897 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.61153
36 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.016694 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.61268
37 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 19 | 5.2778e-05 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.5072
38 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 19 | 0.00023889 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52853
39 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1238.2413 | 20.8591 | 55.3271 | 32.7032 | 35 | 0.0112 | 2 | 23.1101 | 0.0112 | 0.6 | 19 | 0.0013528 | 23.1101 | 0.0112 | NA | NA | 0.91461 | 0.61844
40 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1241.0277 | 20.8807 | 55.3262 | 32.7001 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 0.6 | 19 | 0.0027528 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.65591
41 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1242.4247 | 20.8916 | 55.3257 | 32.6986 | 35 | 0.0112 | 2 | 21.9594 | 0.0112 | 0.6 | 19 | 0.0055528 | 21.9594 | 0.0112 | NA | NA | 1.0031 | 0.67839
42 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 19 | 0.0083139 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.68761
43 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 19 | 0.011122 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69107
44 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 19 | 0.013897 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69395
45 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.8242 | 20.9024 | 55.3252 | 32.6971 | 35 | 0.0112 | 2 | 21.5759 | 0.0112 | 0.6 | 19 | 0.016708 | 21.5759 | 0.0112 | NA | NA | 1.0326 | 0.6951
46 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 17 | 6.6667e-05 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.517
47 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1233.3895 | 20.8214 | 55.3288 | 32.7085 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 0.6 | 17 | 0.00026389 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.54524
48 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1241.7259 | 20.8862 | 55.3259 | 32.6994 | 35 | 0.0112 | 2 | 22.1512 | 0.0112 | 0.6 | 17 | 0.0013667 | 22.1512 | 0.0112 | NA | NA | 0.98837 | 0.66686
49 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1245.2263 | 20.9133 | 55.3248 | 32.6956 | 35 | 0.0112 | 2 | 21.1923 | 0.0112 | 0.6 | 17 | 0.0027278 | 21.1923 | 0.0112 | NA | NA | 1.0621 | 0.71931
50 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1247.3343 | 20.9296 | 55.324 | 32.6933 | 35 | 0.0112 | 2 | 20.617 | 0.0112 | 0.6 | 17 | 0.0055139 | 20.617 | 0.0112 | NA | NA | 1.1064 | 0.75389
51 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1248.7428 | 20.9405 | 55.3236 | 32.6918 | 35 | 0.0112 | 2 | 20.2335 | 0.0112 | 0.6 | 17 | 0.0083139 | 20.2335 | 0.0112 | NA | NA | 1.1359 | 0.76715
52 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1248.7428 | 20.9405 | 55.3236 | 32.6918 | 35 | 0.0112 | 2 | 20.2335 | 0.0112 | 0.6 | 17 | 0.0111 | 20.2335 | 0.0112 | NA | NA | 1.1359 | 0.77406
53 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1249.448 | 20.9459 | 55.3233 | 32.691 | 35 | 0.0112 | 2 | 20.0417 | 0.0112 | 0.6 | 17 | 0.013886 | 20.0417 | 0.0112 | NA | NA | 1.1506 | 0.77637
54 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1249.448 | 20.9459 | 55.3233 | 32.691 | 35 | 0.0112 | 2 | 20.0417 | 0.0112 | 0.6 | 17 | 0.016694 | 20.0417 | 0.0112 | NA | NA | 1.1506 | 0.77983
55 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 27 | 6.3889e-05 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44859
56 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.827 | 20.7626 | 55.3314 | 32.7169 | 35 | 0.0112 | 2 | 26.562 | 0.0112 | 0.6 | 27 | 0.00032778 | 26.562 | 0.0112 | NA | NA | 0.64908 | 0.44011
57 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1224.4601 | 20.7519 | 55.3319 | 32.7184 | 35 | 0.0112 | 2 | 26.9455 | 0.0112 | 0.6 | 27 | 0.0013972 | 26.9455 | 0.0112 | NA | NA | 0.61957 | 0.41808
58 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.0956 | 20.7412 | 55.3323 | 32.7199 | 35 | 0.0112 | 2 | 27.3291 | 0.0112 | 0.6 | 27 | 0.0027583 | 27.3291 | 0.0112 | NA | NA | 0.59007 | 0.4
59 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 27 | 0.0055528 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.38249
60 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 27 | 0.0083472 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.37514
61 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27 | 0.011156 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.37006
62 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27 | 0.013914 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.3678
63 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27 | 0.016733 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.36554
64 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.00023889 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45198
65 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 25 | 0.0013722 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45763
66 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 25 | 0.0027694 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45537
67 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.0055667 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45141
68 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.0083361 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44915
69 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.011156 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44746
70 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.013928 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44689
71 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25 | 0.016697 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44633
72 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 23 | 0.00026389 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.46441
73 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 23 | 0.0013972 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.49774
74 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 23 | 0.0027694 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.51299
75 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 23 | 0.0055667 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.52034
76 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 23 | 0.0083611 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.52429
77 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.011131 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52599
78 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.013914 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52599
79 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23 | 0.016697 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52768
80 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 55.3304 | 32.7138 | 35 | 0.0112 | 2 | 25.7949 | 0.0112 | 0.6 | 21 | 0.00027778 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.4774
81 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.6989 | 20.8161 | 55.329 | 32.7092 | 35 | 0.0112 | 2 | 24.6443 | 0.0112 | 0.6 | 21 | 0.0013722 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.53955
82 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.7726 | 20.8322 | 55.3283 | 32.707 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 0.6 | 21 | 0.0027583 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.57006
83 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.1582 | 20.843 | 55.3278 | 32.7054 | 35 | 0.0112 | 2 | 23.6854 | 0.0112 | 0.6 | 21 | 0.0055417 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.59153
84 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.852 | 20.8483 | 55.3276 | 32.7047 | 35 | 0.0112 | 2 | 23.4936 | 0.0112 | 0.6 | 21 | 0.0083361 | 23.4936 | 0.0112 | NA | NA | 0.88511 | 0.6
85 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.011131 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.60508
86 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.013928 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.60734
87 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 21 | 0.016708 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.60904
88 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.2552 | 20.7893 | 55.3302 | 32.7131 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.6 | 19 | 0.00028889 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.49266
89 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1235.4651 | 20.8376 | 55.3281 | 32.7062 | 35 | 0.0112 | 2 | 23.8772 | 0.0112 | 0.6 | 19 | 0.0013611 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.58249
90 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1238.937 | 20.8645 | 55.3269 | 32.7024 | 35 | 0.0112 | 2 | 22.9183 | 0.0112 | 0.6 | 19 | 0.0027833 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.62938
91 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1241.0277 | 20.8807 | 55.3262 | 32.7001 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 0.6 | 19 | 0.0055417 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.66384
92 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1242.4247 | 20.8916 | 55.3257 | 32.6986 | 35 | 0.0112 | 2 | 21.9594 | 0.0112 | 0.6 | 19 | 0.0083611 | 21.9594 | 0.0112 | NA | NA | 1.0031 | 0.67684
93 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1242.4247 | 20.8916 | 55.3257 | 32.6986 | 35 | 0.0112 | 2 | 21.9594 | 0.0112 | 0.6 | 19 | 0.011119 | 21.9594 | 0.0112 | NA | NA | 1.0031 | 0.68362
94 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 19 | 0.013928 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.6887
95 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 19 | 0.016733 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69153
96 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 17 | 0.00027778 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.50339
97 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1238.937 | 20.8645 | 55.3269 | 32.7024 | 35 | 0.0112 | 2 | 22.9183 | 0.0112 | 0.6 | 17 | 0.0013722 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.62768
98 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 17 | 0.0027444 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.68983
99 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1246.631 | 20.9241 | 55.3243 | 32.694 | 35 | 0.0112 | 2 | 20.8088 | 0.0112 | 0.6 | 17 | 0.0055528 | 20.8088 | 0.0112 | NA | NA | 1.0916 | 0.73616
100 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1247.3343 | 20.9296 | 55.324 | 32.6933 | 35 | 0.0112 | 2 | 20.617 | 0.0112 | 0.6 | 17 | 0.0083111 | 20.617 | 0.0112 | NA | NA | 1.1064 | 0.75367
101 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1248.0382 | 20.935 | 55.3238 | 32.6925 | 35 | 0.0112 | 2 | 20.4252 | 0.0112 | 0.6 | 17 | 0.011119 | 20.4252 | 0.0112 | NA | NA | 1.1211 | 0.76384
102 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1248.7428 | 20.9405 | 55.3236 | 32.6918 | 35 | 0.0112 | 2 | 20.2335 | 0.0112 | 0.6 | 17 | 0.013903 | 20.2335 | 0.0112 | NA | NA | 1.1359 | 0.77006
103 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1248.7428 | 20.9405 | 55.3236 | 32.6918 | 35 | 0.0112 | 2 | 20.2335 | 0.0112 | 0.6 | 17 | 0.016697 | 20.2335 | 0.0112 | NA | NA | 1.1359 | 0.77345
104 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.6989 | 20.8161 | 55.329 | 32.7092 | 35 | 0.0112 | 2 | 24.6443 | 0.0112 | 0.6 | 16.9919 | 0.00027778 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.54453
105 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 18.9919 | 0.00027778 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52907
106 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 21.0081 | 0.00027778 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.5168
107 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 23 | 0.00027778 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.5008
108 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.2552 | 20.7893 | 55.3302 | 32.7131 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.6 | 25.0323 | 0.00027778 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.4864
109 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 55.3307 | 32.7146 | 35 | 0.0112 | 2 | 25.9867 | 0.0112 | 0.6 | 27.0403 | 0.00027778 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.47307
110 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1245.2263 | 20.9133 | 55.3248 | 32.6956 | 35 | 0.0112 | 2 | 21.1923 | 0.0112 | 0.6 | 17.0161 | 0.0027778 | 21.1923 | 0.0112 | NA | NA | 1.0621 | 0.72053
111 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1241.0277 | 20.8807 | 55.3262 | 32.7001 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 0.6 | 19.0323 | 0.0027778 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.656
112 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.1582 | 20.843 | 55.3278 | 32.7054 | 35 | 0.0112 | 2 | 23.6854 | 0.0112 | 0.6 | 21.0403 | 0.0027778 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.5936
113 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 23.0323 | 0.0027778 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.5312
114 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 55.3307 | 32.7146 | 35 | 0.0112 | 2 | 25.9867 | 0.0112 | 0.6 | 25.0403 | 0.0027778 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.46827
115 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 27.0403 | 0.0027778 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40747
116 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.0956 | 20.7412 | 55.3323 | 32.7199 | 35 | 0.0112 | 2 | 27.3291 | 0.0112 | 0.6 | 17 | 0.00027778 | 27.3291 | 0.0112 | NA | NA | 0.59007 | 0.39573
117 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 19.0081 | 0.00027778 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.38933
118 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 21.0403 | 0.00027778 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.38347
119 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 23.0484 | 0.00027778 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.3776
120 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 25.0323 | 0.00027778 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.37173
121 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.0535 | 20.7253 | 55.3331 | 32.7222 | 35 | 0.0112 | 2 | 27.9044 | 0.0112 | 0.6 | 27.0484 | 0.00027778 | 27.9044 | 0.0112 | NA | NA | 0.54582 | 0.36747
122 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1239.6333 | 20.8699 | 55.3266 | 32.7016 | 35 | 0.0112 | 2 | 22.7265 | 0.0112 | 0.6 | 17 | 0.0027778 | 22.7265 | 0.0112 | NA | NA | 0.94411 | 0.64107
123 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.7726 | 20.8322 | 55.3283 | 32.707 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 0.6 | 19 | 0.0027778 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.57387
124 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 21.0323 | 0.0027778 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.50933
125 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.827 | 20.7626 | 55.3314 | 32.7169 | 35 | 0.0112 | 2 | 26.562 | 0.0112 | 0.6 | 23.0323 | 0.0027778 | 26.562 | 0.0112 | NA | NA | 0.64908 | 0.44373
126 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 25.0403 | 0.0027778 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.38187
127 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1217.6623 | 20.6988 | 55.3343 | 32.726 | 35 | 0.0112 | 2 | 28.8633 | 0.0112 | 0.6 | 27.0403 | 0.0027778 | 28.8633 | 0.0112 | NA | NA | 0.47206 | 0.32213
128 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 16.9919 | 0.00027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.46187
129 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 19.0161 | 0.00027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45867
130 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 21.0242 | 0.00027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.4576
131 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 23.0161 | 0.00027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45387
132 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25.0403 | 0.00027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45173
133 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 27.0403 | 0.00027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44907
134 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.0807 | 20.8268 | 55.3285 | 32.7077 | 35 | 0.0112 | 2 | 24.2607 | 0.0112 | 0.6 | 17.0403 | 0.0027778 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.5584
135 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 19.0242 | 0.0027778 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.50827
136 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 21.0242 | 0.0027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.4576
137 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 23.0645 | 0.0027778 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.408
138 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1220.3741 | 20.72 | 55.3333 | 32.7229 | 35 | 0.0112 | 2 | 28.0962 | 0.0112 | 0.6 | 25.0242 | 0.0027778 | 28.0962 | 0.0112 | NA | NA | 0.53106 | 0.36213
139 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1217.6623 | 20.6988 | 55.3343 | 32.726 | 35 | 0.0112 | 2 | 28.8633 | 0.0112 | 0.6 | 27.0645 | 0.0027778 | 28.8633 | 0.0112 | NA | NA | 0.47206 | 0.31787
140 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1224.4601 | 20.7519 | 55.3319 | 32.7184 | 35 | 0.0112 | 2 | 26.9455 | 0.0112 | 0.6 | 17 | 0.00027778 | 26.9455 | 0.0112 | NA | NA | 0.61957 | 0.42293
141 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 19.0242 | 0.00027778 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.41333
142 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.0956 | 20.7412 | 55.3323 | 32.7199 | 35 | 0.0112 | 2 | 27.3291 | 0.0112 | 0.6 | 21.0242 | 0.00027778 | 27.3291 | 0.0112 | NA | NA | 0.59007 | 0.40267
143 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 23.0242 | 0.00027778 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.39307
144 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 25.0403 | 0.00027778 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.3856
145 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 27.0484 | 0.00027778 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.376
146 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1237.5463 | 20.8537 | 55.3273 | 32.7039 | 35 | 0.0112 | 2 | 23.3018 | 0.0112 | 0.6 | 17.0323 | 0.0027778 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.6112
147 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.0807 | 20.8268 | 55.3285 | 32.7077 | 35 | 0.0112 | 2 | 24.2607 | 0.0112 | 0.6 | 19.0161 | 0.0027778 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.56
148 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 21.0323 | 0.0027778 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.50933
149 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 23.0403 | 0.0027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.46027
150 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 25.0161 | 0.0027778 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.41173
151 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1220.3741 | 20.72 | 55.3333 | 32.7229 | 35 | 0.0112 | 2 | 28.0962 | 0.0112 | 0.6 | 27.0484 | 0.0027778 | 28.0962 | 0.0112 | NA | NA | 0.53106 | 0.36213
152 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 16.96 | 0.00027778 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.50583
153 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.2552 | 20.7893 | 55.3302 | 32.7131 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.6 | 18.9657 | 0.00027778 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.49359
154 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 55.3304 | 32.7138 | 35 | 0.0112 | 2 | 25.7949 | 0.0112 | 0.6 | 21.0229 | 0.00027778 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.48019
155 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 55.3307 | 32.7146 | 35 | 0.0112 | 2 | 25.9867 | 0.0112 | 0.6 | 23.0029 | 0.00027778 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.46738
156 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 25.0514 | 0.00027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45515
157 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.827 | 20.7626 | 55.3314 | 32.7169 | 35 | 0.0112 | 2 | 26.562 | 0.0112 | 0.6 | 27.0657 | 0.00027778 | 26.562 | 0.0112 | NA | NA | 0.64908 | 0.44233
158 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 55.3255 | 32.6978 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 0.6 | 16.9857 | 0.0027778 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69282
159 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1238.937 | 20.8645 | 55.3269 | 32.7024 | 35 | 0.0112 | 2 | 22.9183 | 0.0112 | 0.6 | 19.0257 | 0.0027778 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.63282
160 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.7726 | 20.8322 | 55.3283 | 32.707 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 0.6 | 21.0057 | 0.0027778 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.5734
161 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 23.0286 | 0.0027778 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.51689
162 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 25.0343 | 0.0027778 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45806
163 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.0956 | 20.7412 | 55.3323 | 32.7199 | 35 | 0.0112 | 2 | 27.3291 | 0.0112 | 0.6 | 27.04 | 0.0027778 | 27.3291 | 0.0112 | NA | NA | 0.59007 | 0.40039
164 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 17.0114 | 0.00027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.4499
165 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 18.9914 | 0.00027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44583
166 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.827 | 20.7626 | 55.3314 | 32.7169 | 35 | 0.0112 | 2 | 26.562 | 0.0112 | 0.6 | 20.9971 | 0.00027778 | 26.562 | 0.0112 | NA | NA | 0.64908 | 0.44233
167 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.827 | 20.7626 | 55.3314 | 32.7169 | 35 | 0.0112 | 2 | 26.562 | 0.0112 | 0.6 | 23.0114 | 0.00027778 | 26.562 | 0.0112 | NA | NA | 0.64908 | 0.43883
168 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.827 | 20.7626 | 55.3314 | 32.7169 | 35 | 0.0112 | 2 | 26.562 | 0.0112 | 0.6 | 25.0171 | 0.00027778 | 26.562 | 0.0112 | NA | NA | 0.64908 | 0.43534
169 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.1432 | 20.7572 | 55.3316 | 32.7176 | 35 | 0.0112 | 2 | 26.7538 | 0.0112 | 0.6 | 27.0657 | 0.00027778 | 26.7538 | 0.0112 | NA | NA | 0.63433 | 0.43126
170 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1238.937 | 20.8645 | 55.3269 | 32.7024 | 35 | 0.0112 | 2 | 22.9183 | 0.0112 | 0.6 | 17.0114 | 0.0027778 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.63456
171 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1234.7726 | 20.8322 | 55.3283 | 32.707 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 0.6 | 19.0086 | 0.0027778 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.56932
172 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 21.0057 | 0.0027778 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.50699
173 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 23.0114 | 0.0027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44699
174 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 25.0171 | 0.0027778 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.38932
175 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1218.3393 | 20.7041 | 55.334 | 32.7252 | 35 | 0.0112 | 2 | 28.6715 | 0.0112 | 0.6 | 27.04 | 0.0027778 | 28.6715 | 0.0112 | NA | NA | 0.48681 | 0.33165
176 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1224.4601 | 20.7519 | 55.3319 | 32.7184 | 35 | 0.0112 | 2 | 26.9455 | 0.0112 | 0.6 | 16.9771 | 0.00027778 | 26.9455 | 0.0112 | NA | NA | 0.61957 | 0.42369
177 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 18.9743 | 0.00027778 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40971
178 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.0956 | 20.7412 | 55.3323 | 32.7199 | 35 | 0.0112 | 2 | 27.3291 | 0.0112 | 0.6 | 21.0143 | 0.00027778 | 27.3291 | 0.0112 | NA | NA | 0.59007 | 0.39981
179 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 23.0114 | 0.00027778 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.38699
180 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 25.0171 | 0.00027778 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.37883
181 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 55.3328 | 32.7214 | 35 | 0.0112 | 2 | 27.7126 | 0.0112 | 0.6 | 27.0314 | 0.00027778 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.37592
182 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.852 | 20.8483 | 55.3276 | 32.7047 | 35 | 0.0112 | 2 | 23.4936 | 0.0112 | 0.6 | 17.0286 | 0.0027778 | 23.4936 | 0.0112 | NA | NA | 0.88511 | 0.60019
183 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1233.3895 | 20.8214 | 55.3288 | 32.7085 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 0.6 | 19.0257 | 0.0027778 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.54951
184 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 20.9971 | 0.0027778 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.49942
185 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 23.0114 | 0.0027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45282
186 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 55.3321 | 32.7191 | 35 | 0.0112 | 2 | 27.1373 | 0.0112 | 0.6 | 25.0771 | 0.0027778 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40621
187 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1220.3741 | 20.72 | 55.3333 | 32.7229 | 35 | 0.0112 | 2 | 28.0962 | 0.0112 | 0.6 | 27.0657 | 0.0027778 | 28.0962 | 0.0112 | NA | NA | 0.53106 | 0.35961
188 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1233.3895 | 20.8214 | 55.3288 | 32.7085 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 0.6 | 16.9771 | 0.00027778 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.54835
189 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.3292 | 32.71 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.6 | 18.9657 | 0.00027778 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.53146
190 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.3195 | 20.8053 | 55.3295 | 32.7108 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.6 | 21.0143 | 0.00027778 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.51806
191 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 23.0286 | 0.00027778 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.5
192 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 55.3304 | 32.7138 | 35 | 0.0112 | 2 | 25.7949 | 0.0112 | 0.6 | 25.0257 | 0.00027778 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.47961
193 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 55.3307 | 32.7146 | 35 | 0.0112 | 2 | 25.9867 | 0.0112 | 0.6 | 27.0314 | 0.00027778 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.46854
194 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1245.2263 | 20.9133 | 55.3248 | 32.6956 | 35 | 0.0112 | 2 | 21.1923 | 0.0112 | 0.6 | 16.9857 | 0.0027778 | 21.1923 | 0.0112 | NA | NA | 1.0621 | 0.71845
195 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1240.3302 | 20.8753 | 55.3264 | 32.7009 | 35 | 0.0112 | 2 | 22.5348 | 0.0112 | 0.6 | 19 | 0.0027778 | 22.5348 | 0.0112 | NA | NA | 0.95887 | 0.64854
196 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1235.4651 | 20.8376 | 55.3281 | 32.7062 | 35 | 0.0112 | 2 | 23.8772 | 0.0112 | 0.6 | 21.0057 | 0.0027778 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.58272
197 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.6308 | 20.8 | 55.3297 | 32.7115 | 35 | 0.0112 | 2 | 25.2196 | 0.0112 | 0.6 | 23.0629 | 0.0027778 | 25.2196 | 0.0112 | NA | NA | 0.75234 | 0.5134
198 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 55.3311 | 32.7161 | 35 | 0.0112 | 2 | 26.3702 | 0.0112 | 0.6 | 25.0171 | 0.0027778 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44932
199 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.4143 | 20.7359 | 55.3326 | 32.7207 | 35 | 0.0112 | 2 | 27.5209 | 0.0112 | 0.6 | 27.0486 | 0.0027778 | 27.5209 | 0.0112 | NA | NA | 0.57532 | 0.38583
200 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1241.7259 | 20.8862 | 55.3259 | 32.6994 | 35 | 0.0112 | 2 | 22.1512 | 0.0112 | 0.6 | 17 | 0.0013889 | 22.1512 | 0.0112 | NA | NA | 0.98837 | 0.6678
201 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.4 | 1242.4247 | 20.8916 | 55.3257 | 36.9377 | 35 | 0.0112 | 2 | 21.9594 | 0.0112 | 0.8 | 17 | 0.0013889 | 21.9594 | 0.0112 | NA | NA | 1.0031 | 0.67712
202 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.50064 | 1242.4247 | 20.8916 | 55.3257 | 40.695 | 35 | 0.0112 | 2 | 21.9594 | 0.0112 | 1.0013 | 17 | 0.0013889 | 21.9594 | 0.0112 | NA | NA | 1.0031 | 0.68418
203 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.60032 | 1243.1242 | 20.897 | 55.3255 | 44.0587 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 1.2006 | 17 | 0.0013889 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.68955
204 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.7 | 1243.1242 | 20.897 | 55.3255 | 47.1535 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 1.4 | 17 | 0.0013889 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69435
205 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.50339
206 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.40096 | 1231.3195 | 20.8053 | 55.3295 | 36.9861 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.80191 | 17 | 0.0013889 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.5209
207 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.50064 | 1232.6989 | 20.8161 | 55.329 | 40.7031 | 35 | 0.0112 | 2 | 24.6443 | 0.0112 | 1.0013 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.53955
208 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.60096 | 1233.3895 | 20.8214 | 55.3288 | 44.0862 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 1.2019 | 17 | 0.0013889 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.55452
209 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.70096 | 1234.7726 | 20.8322 | 55.3283 | 47.1872 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 1.4019 | 17 | 0.0013889 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.56864
210 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.29968 | 1227.1964 | 20.7732 | 55.3309 | 32.7008 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.59936 | 17 | 0.0013889 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45847
211 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.4 | 1229.2552 | 20.7893 | 55.3302 | 36.9503 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.8 | 17 | 0.0013889 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.49294
212 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.50032 | 1231.3195 | 20.8053 | 55.3295 | 40.6929 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 1.0006 | 17 | 0.0013889 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.52119
213 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.60096 | 1232.6989 | 20.8161 | 55.329 | 44.0867 | 35 | 0.0112 | 2 | 24.6443 | 0.0112 | 1.2019 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.54492
214 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.70032 | 1234.0807 | 20.8268 | 55.3285 | 47.1685 | 35 | 0.0112 | 2 | 24.2607 | 0.0112 | 1.4006 | 17 | 0.0013889 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.56384
215 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.30032 | 1232.6989 | 20.8161 | 55.329 | 32.7238 | 35 | 0.0112 | 2 | 24.6443 | 0.0112 | 0.60064 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.53701
216 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.40032 | 1233.3895 | 20.8214 | 55.3288 | 36.9589 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 0.80064 | 17 | 0.0013889 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.55339
217 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.50064 | 1234.7726 | 20.8322 | 55.3283 | 40.7013 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 1.0013 | 17 | 0.0013889 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.56582
218 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.59968 | 1235.4651 | 20.8376 | 55.3281 | 44.0436 | 35 | 0.0112 | 2 | 23.8772 | 0.0112 | 1.1994 | 17 | 0.0013889 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.57712
219 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.70064 | 1236.1582 | 20.843 | 55.3278 | 47.1768 | 35 | 0.0112 | 2 | 23.6854 | 0.0112 | 1.4013 | 17 | 0.0013889 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.58672
220 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.30064 | 1238.937 | 20.8645 | 55.3269 | 32.7315 | 35 | 0.0112 | 2 | 22.9183 | 0.0112 | 0.60127 | 17 | 0.0013889 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.62994
221 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.4 | 1239.6333 | 20.8699 | 55.3266 | 36.9404 | 35 | 0.0112 | 2 | 22.7265 | 0.0112 | 0.8 | 17 | 0.0013889 | 22.7265 | 0.0112 | NA | NA | 0.94411 | 0.64153
222 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.50096 | 1240.3302 | 20.8753 | 55.3264 | 40.708 | 35 | 0.0112 | 2 | 22.5348 | 0.0112 | 1.0019 | 17 | 0.0013889 | 22.5348 | 0.0112 | NA | NA | 0.95887 | 0.65028
223 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.60127 | 1241.0277 | 20.8807 | 55.3262 | 44.091 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 1.2025 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.65847
224 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.7 | 1241.0277 | 20.8807 | 55.3262 | 47.1548 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 1.4 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.66441
225 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.30096 | 1229.2552 | 20.7893 | 55.3302 | 32.7566 | 35 | 0.0112 | 2 | 25.6031 | 0.0112 | 0.60191 | 17 | 0.0013889 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.4935
226 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.4 | 1231.3195 | 20.8053 | 55.3295 | 36.9483 | 35 | 0.0112 | 2 | 25.0278 | 0.0112 | 0.8 | 17 | 0.0013889 | 25.0278 | 0.0112 | NA | NA | 0.76709 | 0.52373
227 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.50127 | 1233.3895 | 20.8214 | 55.3288 | 40.725 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 1.0025 | 17 | 0.0013889 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.55028
228 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.6 | 1234.7726 | 20.8322 | 55.3283 | 44.0544 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 1.2 | 17 | 0.0013889 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.57316
229 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.70159 | 1236.1582 | 20.843 | 55.3278 | 47.2053 | 35 | 0.0112 | 2 | 23.6854 | 0.0112 | 1.4032 | 17 | 0.0013889 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.59096
230 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.29968 | 1232.0089 | 20.8107 | 55.3292 | 32.6955 | 35 | 0.0112 | 2 | 24.836 | 0.0112 | 0.59936 | 17 | 0.0013889 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52881
231 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.40032 | 1233.3895 | 20.8214 | 55.3288 | 36.9589 | 35 | 0.0112 | 2 | 24.4525 | 0.0112 | 0.80064 | 17 | 0.0013889 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.54605
232 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.50032 | 1234.0807 | 20.8268 | 55.3285 | 40.6906 | 35 | 0.0112 | 2 | 24.2607 | 0.0112 | 1.0006 | 17 | 0.0013889 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.56073
233 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.60032 | 1234.7726 | 20.8322 | 55.3283 | 44.0647 | 35 | 0.0112 | 2 | 24.0689 | 0.0112 | 1.2006 | 17 | 0.0013889 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.57345
234 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.70032 | 1235.4651 | 20.8376 | 55.3281 | 47.1677 | 35 | 0.0112 | 2 | 23.8772 | 0.0112 | 1.4006 | 17 | 0.0013889 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.5839
235 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.30032 | 1241.0277 | 20.8807 | 55.3262 | 32.7147 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 0.60064 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.65508
236 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.40064 | 1241.0277 | 20.8807 | 55.3262 | 36.9642 | 35 | 0.0112 | 2 | 22.343 | 0.0112 | 0.80127 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.66412
237 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.50064 | 1241.7259 | 20.8862 | 55.3259 | 40.6956 | 35 | 0.0112 | 2 | 22.1512 | 0.0112 | 1.0013 | 17 | 0.0013889 | 22.1512 | 0.0112 | NA | NA | 0.98837 | 0.67175
238 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.60096 | 1242.4247 | 20.8916 | 55.3257 | 44.0798 | 35 | 0.0112 | 2 | 21.9594 | 0.0112 | 1.2019 | 17 | 0.0013889 | 21.9594 | 0.0112 | NA | NA | 1.0031 | 0.67938
239 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.7 | 1243.1242 | 20.897 | 55.3255 | 47.1535 | 35 | 0.0112 | 2 | 21.7677 | 0.0112 | 1.4 | 17 | 0.0013889 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.68616
240 | PCC | 0.5 | 0.0030063 | 0.5 | 1 | 0.3 | 1256.5357 | 21.0006 | 92.0091 | 54.3585 | 35 | 0.0112 | 3.3264 | 18.124 | 0.0112 | 0.99791 | 17 | 0.0013889 | 18.124 | 0.0112 | NA | NA | 1.2982 | 0.88391
241 | PCC | 0.5 | 0.0039953 | 0.5 | 1 | 0.3 | 1249.448 | 20.9459 | 69.2357 | 40.9119 | 35 | 0.0112 | 2.5029 | 20.0417 | 0.0112 | 0.75088 | 17 | 0.0013889 | 20.0417 | 0.0112 | NA | NA | 1.1506 | 0.77874
242 | PCC | 0.5 | 0.0050063 | 0.5 | 1 | 0.3 | 1241.7259 | 20.8862 | 55.2565 | 32.6583 | 35 | 0.0112 | 1.9975 | 22.1512 | 0.0112 | 0.59925 | 17 | 0.0013889 | 22.1512 | 0.0112 | NA | NA | 0.98837 | 0.67069
243 | PCC | 0.5 | 0.0059984 | 0.5 | 1 | 0.3 | 1235.4651 | 20.8376 | 46.1188 | 27.2623 | 35 | 0.0112 | 1.6671 | 23.8772 | 0.0112 | 0.50013 | 17 | 0.0013889 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.57529
244 | PCC | 0.5 | 0.0070126 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 39.4506 | 23.3241 | 35 | 0.0112 | 1.426 | 25.4113 | 0.0112 | 0.4278 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.49885
245 | PCP | 0.5 | 0.0029937 | 0.5 | 1 | 0.3 | 1243.1242 | 20.897 | 92.4025 | 54.6107 | 35 | 0.0112 | 3.3403 | 21.7677 | 0.0112 | 1.0021 | 17 | 0.0013889 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69368
246 | PCP | 0.5 | 0.0040016 | 0.5 | 1 | 0.3 | 1235.4651 | 20.8376 | 69.1329 | 40.8667 | 35 | 0.0112 | 2.499 | 23.8772 | 0.0112 | 0.74971 | 17 | 0.0013889 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.57529
247 | PCP | 0.5 | 0.0050063 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.2606 | 32.6713 | 35 | 0.0112 | 1.9975 | 25.4113 | 0.0112 | 0.59925 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.5046
248 | PCP | 0.5 | 0.0060047 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 46.0731 | 27.242 | 35 | 0.0112 | 1.6654 | 26.3702 | 0.0112 | 0.49961 | 17 | 0.0013889 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44885
249 | PCP | 0.5 | 0.0070094 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 39.4698 | 23.3394 | 35 | 0.0112 | 1.4267 | 27.1373 | 0.0112 | 0.428 | 17 | 0.0013889 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40632
250 | PPC | 0.5 | 0.0030063 | 0.5 | 1 | 0.3 | 1233.3895 | 20.8214 | 92.022 | 54.4003 | 35 | 0.0112 | 3.3264 | 24.4525 | 0.0112 | 0.99791 | 17 | 0.0013889 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.5477
251 | PPC | 0.5 | 0.0040078 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 69.027 | 40.8103 | 35 | 0.0112 | 2.4951 | 25.4113 | 0.0112 | 0.74853 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.50115
252 | PPC | 0.5 | 0.0050031 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.2962 | 32.6948 | 35 | 0.0112 | 1.9987 | 26.1784 | 0.0112 | 0.59962 | 17 | 0.0013889 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.46034
253 | PPC | 0.5 | 0.0059984 | 0.5 | 1 | 0.3 | 1224.4601 | 20.7519 | 46.122 | 27.2724 | 35 | 0.0112 | 1.6671 | 26.9455 | 0.0112 | 0.50013 | 17 | 0.0013889 | 26.9455 | 0.0112 | NA | NA | 0.61957 | 0.42011
254 | PPC | 0.5 | 0.0070094 | 0.5 | 1 | 0.3 | 1221.7336 | 20.7306 | 39.4703 | 23.341 | 35 | 0.0112 | 1.4267 | 27.7126 | 0.0112 | 0.428 | 17 | 0.0013889 | 27.7126 | 0.0112 | NA | NA | 0.56057 | 0.38103
255 | PPP | 0.5 | 0.0030063 | 0.5 | 1 | 0.3 | 1241.0277 | 20.8807 | 92.0177 | 54.3864 | 35 | 0.0112 | 3.3264 | 22.343 | 0.0112 | 0.99791 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.65747
256 | PPP | 0.5 | 0.0039984 | 0.5 | 1 | 0.3 | 1236.852 | 20.8483 | 69.1866 | 40.8969 | 35 | 0.0112 | 2.501 | 23.4936 | 0.0112 | 0.75029 | 17 | 0.0013889 | 23.4936 | 0.0112 | NA | NA | 0.88511 | 0.59713
257 | PPP | 0.5 | 0.0049969 | 0.5 | 1 | 0.3 | 1232.6989 | 20.8161 | 55.3638 | 32.7298 | 35 | 0.0112 | 2.0013 | 24.6443 | 0.0112 | 0.60038 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.53908
258 | PPP | 0.5 | 0.0060047 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 46.0725 | 27.2401 | 35 | 0.0112 | 1.6654 | 25.7949 | 0.0112 | 0.49961 | 17 | 0.0013889 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.48161
259 | PPP | 0.5 | 0.0070094 | 0.5 | 1 | 0.3 | 1225.1432 | 20.7572 | 39.4695 | 23.3383 | 35 | 0.0112 | 1.4267 | 26.7538 | 0.0112 | 0.428 | 17 | 0.0013889 | 26.7538 | 0.0112 | NA | NA | 0.63433 | 0.42989
260 | XPP | 0.5 | 0.003 | 0.5 | 1 | 0.3 | 1253.6928 | 20.9787 | 92.2032 | 54.4774 | 35 | 0.0112 | 3.3333 | 18.8911 | 0.0112 | 1 | 17 | 0.0013889 | 18.8911 | 0.0112 | NA | NA | 1.2391 | 0.84195
261 | XPP | 0.5 | 0.0039922 | 0.5 | 1 | 0.3 | 1245.9283 | 20.9187 | 69.2916 | 40.9488 | 35 | 0.0112 | 2.5049 | 21.0006 | 0.0112 | 0.75147 | 17 | 0.0013889 | 21.0006 | 0.0112 | NA | NA | 1.0769 | 0.73218
262 | XPP | 0.5 | 0.0049937 | 0.5 | 1 | 0.3 | 1238.937 | 20.8645 | 55.3964 | 32.7435 | 35 | 0.0112 | 2.0025 | 22.9183 | 0.0112 | 0.60075 | 17 | 0.0013889 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.63218
263 | XPP | 0.5 | 0.0060047 | 0.5 | 1 | 0.3 | 1233.3895 | 20.8214 | 46.0711 | 27.2357 | 35 | 0.0112 | 1.6654 | 24.4525 | 0.0112 | 0.49961 | 17 | 0.0013889 | 24.4525 | 0.0112 | NA | NA | 0.81135 | 0.5454
264 | XPP | 0.5 | 0.0070063 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 39.4863 | 23.3461 | 35 | 0.0112 | 1.4273 | 25.7949 | 0.0112 | 0.42819 | 17 | 0.0013889 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.47586
265 | XPC | 0.5 | 0.0030063 | 0.5 | 1 | 0.3 | 1238.937 | 20.8645 | 92.0189 | 54.3902 | 35 | 0.0112 | 3.3264 | 22.9183 | 0.0112 | 0.99791 | 17 | 0.0013889 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.63046
266 | XPC | 0.5 | 0.004011 | 0.5 | 1 | 0.3 | 1232.6989 | 20.8161 | 68.9718 | 40.7745 | 35 | 0.0112 | 2.4932 | 24.6443 | 0.0112 | 0.74795 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.54425
267 | XPC | 0.5 | 0.0050063 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.2606 | 32.6713 | 35 | 0.0112 | 1.9975 | 25.4113 | 0.0112 | 0.59925 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.4954
268 | XPC | 0.5 | 0.0060047 | 0.5 | 1 | 0.3 | 1226.5114 | 20.7679 | 46.0731 | 27.242 | 35 | 0.0112 | 1.6654 | 26.3702 | 0.0112 | 0.49961 | 17 | 0.0013889 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.44885
269 | XPC | 0.5 | 0.0070094 | 0.5 | 1 | 0.3 | 1223.7775 | 20.7466 | 39.4698 | 23.3394 | 35 | 0.0112 | 1.4267 | 27.1373 | 0.0112 | 0.428 | 17 | 0.0013889 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40632
270 | PCX | 0.5 | 0.0029937 | 0.5 | 1 | 0.3 | 1241.7259 | 20.8862 | 92.4033 | 54.6132 | 35 | 0.0112 | 3.3403 | 22.1512 | 0.0112 | 1.0021 | 17 | 0.0013889 | 22.1512 | 0.0112 | NA | NA | 0.98837 | 0.66954
271 | PCX | 0.5 | 0.0039984 | 0.5 | 1 | 0.3 | 1236.852 | 20.8483 | 69.1866 | 40.8969 | 35 | 0.0112 | 2.501 | 23.4936 | 0.0112 | 0.75029 | 17 | 0.0013889 | 23.4936 | 0.0112 | NA | NA | 0.88511 | 0.59713
272 | PCX | 0.5 | 0.0050031 | 0.5 | 1 | 0.3 | 1232.0089 | 20.8107 | 55.2945 | 32.6895 | 35 | 0.0112 | 1.9987 | 24.836 | 0.0112 | 0.59962 | 17 | 0.0013889 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52931
273 | PCX | 0.5 | 0.0060078 | 0.5 | 1 | 0.3 | 1227.8821 | 20.7786 | 46.0486 | 27.2265 | 35 | 0.0112 | 1.6645 | 25.9867 | 0.0112 | 0.49935 | 17 | 0.0013889 | 25.9867 | 0.0112 | NA | NA | 0.69333 | 0.47069
274 | PCX | 0.5 | 0.0070063 | 0.5 | 1 | 0.3 | 1224.4601 | 20.7519 | 39.4873 | 23.3493 | 35 | 0.0112 | 1.4273 | 26.9455 | 0.0112 | 0.42819 | 17 | 0.0013889 | 26.9455 | 0.0112 | NA | NA | 0.61957 | 0.41667
275 | PPX | 0.5 | 0.0030031 | 0.5 | 1 | 0.3 | 1257.248 | 21.0061 | 92.1049 | 54.4141 | 35 | 0.0112 | 3.3298 | 17.9322 | 0.0112 | 0.99895 | 17 | 0.0013889 | 17.9322 | 0.0112 | NA | NA | 1.3129 | 0.8908
276 | PPX | 0.5 | 0.0040016 | 0.5 | 1 | 0.3 | 1249.448 | 20.9459 | 69.127 | 40.8477 | 35 | 0.0112 | 2.499 | 20.0417 | 0.0112 | 0.74971 | 17 | 0.0013889 | 20.0417 | 0.0112 | NA | NA | 1.1506 | 0.78276
277 | PPX | 0.5 | 0.0050094 | 0.5 | 1 | 0.3 | 1241.0277 | 20.8807 | 55.2221 | 32.6386 | 35 | 0.0112 | 1.9962 | 22.343 | 0.0112 | 0.59887 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.65632
278 | PPX | 0.5 | 0.0059984 | 0.5 | 1 | 0.3 | 1234.0807 | 20.8268 | 46.1192 | 27.2636 | 35 | 0.0112 | 1.6671 | 24.2607 | 0.0112 | 0.50013 | 17 | 0.0013889 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.56207
279 | PPX | 0.5 | 0.0070063 | 0.5 | 1 | 0.3 | 1228.5683 | 20.7839 | 39.4863 | 23.3461 | 35 | 0.0112 | 1.4273 | 25.7949 | 0.0112 | 0.42819 | 17 | 0.0013889 | 25.7949 | 0.0112 | NA | NA | 0.70809 | 0.48448
280 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 623.5298 | 15.3844 | 40.5695 | 24.6062 | 35 | 0.0112 | 0.99471 | 18.8911 | 0.0112 | 0.29841 | 17 | 0.0013889 | 18.8911 | 0.0112 | NA | NA | 1.2391 | 0.83951
281 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 933.1908 | 18.3732 | 48.5668 | 28.9922 | 35 | 0.0112 | 1.4963 | 20.617 | 0.0112 | 0.44889 | 17 | 0.0013889 | 20.617 | 0.0112 | NA | NA | 1.1064 | 0.74537
282 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1235.1559 | 20.8361 | 55.1934 | 32.6268 | 35 | 0.0112 | 1.9894 | 22.1512 | 0.0112 | 0.59683 | 17 | 0.0013889 | 22.1512 | 0.0112 | NA | NA | 0.98837 | 0.66829
283 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1542.6768 | 23.0501 | 61.1546 | 35.8956 | 35 | 0.0112 | 2.4931 | 23.3018 | 0.0112 | 0.74794 | 17 | 0.0013889 | 23.3018 | 0.0112 | NA | NA | 0.89986 | 0.60585
284 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1846.5506 | 25.0296 | 66.4936 | 38.8231 | 35 | 0.0112 | 2.9926 | 24.2607 | 0.0112 | 0.89778 | 17 | 0.0013889 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.55561
285 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 621.3367 | 15.3601 | 40.6128 | 24.6362 | 35 | 0.0112 | 0.99683 | 20.8088 | 0.0112 | 0.29905 | 17 | 0.0013889 | 20.8088 | 0.0112 | NA | NA | 1.0916 | 0.73561
286 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 924.8295 | 18.2983 | 48.5731 | 29.0057 | 35 | 0.0112 | 1.4963 | 23.6854 | 0.0112 | 0.44889 | 17 | 0.0013889 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.58878
287 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1229.9427 | 20.7946 | 55.33 | 32.7123 | 35 | 0.0112 | 2 | 25.4113 | 0.0112 | 0.6 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.50293
288 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1536.7086 | 23.0076 | 61.2982 | 35.9844 | 35 | 0.0112 | 2.5058 | 26.3702 | 0.0112 | 0.75175 | 17 | 0.0013889 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.4522
289 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1833.7238 | 24.9476 | 66.5365 | 38.856 | 35 | 0.0112 | 2.9968 | 27.1373 | 0.0112 | 0.89905 | 17 | 0.0013889 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.41463
290 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 618.7332 | 15.331 | 40.6964 | 24.6915 | 35 | 0.0112 | 1.0011 | 23.6854 | 0.0112 | 0.30032 | 17 | 0.0013889 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.58634
291 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 920.1793 | 18.2565 | 48.5766 | 29.0133 | 35 | 0.0112 | 1.4963 | 25.4113 | 0.0112 | 0.44889 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.50488
292 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.1964 | 20.7732 | 55.3309 | 32.7153 | 35 | 0.0112 | 2 | 26.1784 | 0.0112 | 0.6 | 17 | 0.0013889 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.45854
293 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1528.5122 | 22.9512 | 61.1801 | 35.921 | 35 | 0.0112 | 2.4952 | 26.7538 | 0.0112 | 0.74857 | 17 | 0.0013889 | 26.7538 | 0.0112 | NA | NA | 0.63433 | 0.42829
294 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1827.2488 | 24.9071 | 66.4283 | 38.7968 | 35 | 0.0112 | 2.9862 | 27.1373 | 0.0112 | 0.89587 | 17 | 0.0013889 | 27.1373 | 0.0112 | NA | NA | 0.60482 | 0.40634
295 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 615.9175 | 15.3012 | 40.5424 | 24.6027 | 35 | 0.0112 | 0.99259 | 22.343 | 0.0112 | 0.29778 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.66439
296 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 926.1376 | 18.3098 | 48.6036 | 29.0225 | 35 | 0.0112 | 1.4984 | 23.6854 | 0.0112 | 0.44952 | 17 | 0.0013889 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.5922
297 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.09 | 20.7962 | 55.2761 | 32.6802 | 35 | 0.0112 | 1.9958 | 24.6443 | 0.0112 | 0.59873 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.53659
298 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1537.103 | 23.0108 | 61.2267 | 35.9421 | 35 | 0.0112 | 2.4995 | 25.4113 | 0.0112 | 0.74984 | 17 | 0.0013889 | 25.4113 | 0.0112 | NA | NA | 0.73759 | 0.49561
299 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1838.8467 | 24.9802 | 66.5366 | 38.8529 | 35 | 0.0112 | 2.9968 | 26.1784 | 0.0112 | 0.89905 | 17 | 0.0013889 | 26.1784 | 0.0112 | NA | NA | 0.67858 | 0.46146
300 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 618.1501 | 15.3263 | 40.459 | 24.5482 | 35 | 0.0112 | 0.98836 | 19.6582 | 0.0112 | 0.29651 | 17 | 0.0013889 | 19.6582 | 0.0112 | NA | NA | 1.1801 | 0.80049
301 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 930.5648 | 18.3498 | 48.5687 | 28.9964 | 35 | 0.0112 | 1.4963 | 21.5759 | 0.0112 | 0.44889 | 17 | 0.0013889 | 21.5759 | 0.0112 | NA | NA | 1.0326 | 0.7039
302 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.3149 | 20.8446 | 55.2739 | 32.6734 | 35 | 0.0112 | 1.9958 | 22.9183 | 0.0112 | 0.59873 | 17 | 0.0013889 | 22.9183 | 0.0112 | NA | NA | 0.92936 | 0.62927
303 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1537.9125 | 23.0171 | 61.1313 | 35.8854 | 35 | 0.0112 | 2.491 | 24.0689 | 0.0112 | 0.7473 | 17 | 0.0013889 | 24.0689 | 0.0112 | NA | NA | 0.84085 | 0.57171
304 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1839.5392 | 24.9854 | 66.4286 | 38.7894 | 35 | 0.0112 | 2.9862 | 24.836 | 0.0112 | 0.89587 | 17 | 0.0013889 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52585
305 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 622.2198 | 15.3693 | 40.6906 | 24.682 | 35 | 0.0112 | 1.0011 | 21.7677 | 0.0112 | 0.30032 | 17 | 0.0013889 | 21.7677 | 0.0112 | NA | NA | 1.0179 | 0.69463
306 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 925.887 | 18.3074 | 48.6354 | 29.0417 | 35 | 0.0112 | 1.5005 | 24.2607 | 0.0112 | 0.45016 | 17 | 0.0013889 | 24.2607 | 0.0112 | NA | NA | 0.8261 | 0.56146
307 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.556 | 20.7992 | 55.3566 | 32.7275 | 35 | 0.0112 | 2.0021 | 25.6031 | 0.0112 | 0.60063 | 17 | 0.0013889 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.49268
308 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1536.7086 | 23.0076 | 61.2982 | 35.9844 | 35 | 0.0112 | 2.5058 | 26.3702 | 0.0112 | 0.75175 | 17 | 0.0013889 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.4522
309 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1836.0423 | 24.9622 | 66.5581 | 38.8672 | 35 | 0.0112 | 2.9989 | 26.9455 | 0.0112 | 0.89968 | 17 | 0.0013889 | 26.9455 | 0.0112 | NA | NA | 0.61957 | 0.42293
310 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 615.9175 | 15.3012 | 40.5424 | 24.6027 | 35 | 0.0112 | 0.99259 | 22.343 | 0.0112 | 0.29778 | 17 | 0.0013889 | 22.343 | 0.0112 | NA | NA | 0.97362 | 0.66
311 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 921.6962 | 18.2706 | 48.5122 | 28.973 | 35 | 0.0112 | 1.4921 | 23.8772 | 0.0112 | 0.44762 | 17 | 0.0013889 | 23.8772 | 0.0112 | NA | NA | 0.8556 | 0.58488
312 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1233.3126 | 20.8207 | 55.3557 | 32.7245 | 35 | 0.0112 | 2.0021 | 24.836 | 0.0112 | 0.60063 | 17 | 0.0013889 | 24.836 | 0.0112 | NA | NA | 0.78184 | 0.52927
313 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1532.3414 | 22.9781 | 61.1558 | 35.9039 | 35 | 0.0112 | 2.4931 | 25.6031 | 0.0112 | 0.74794 | 17 | 0.0013889 | 25.6031 | 0.0112 | NA | NA | 0.72284 | 0.48634
314 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1837.8203 | 24.9737 | 66.5366 | 38.8536 | 35 | 0.0112 | 2.9968 | 26.3702 | 0.0112 | 0.89905 | 17 | 0.0013889 | 26.3702 | 0.0112 | NA | NA | 0.66383 | 0.45415
315 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 627.1548 | 15.4232 | 40.6826 | 24.6687 | 35 | 0.0112 | 1.0011 | 19.0828 | 0.0112 | 0.30032 | 17 | 0.0013889 | 19.0828 | 0.0112 | NA | NA | 1.2244 | 0.83024
316 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 936.0943 | 18.3985 | 48.6593 | 29.0441 | 35 | 0.0112 | 1.5026 | 21.0006 | 0.0112 | 0.45079 | 17 | 0.0013889 | 21.0006 | 0.0112 | NA | NA | 1.0769 | 0.73415
317 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1236.3926 | 20.8454 | 55.2469 | 32.6574 | 35 | 0.0112 | 1.9937 | 22.5348 | 0.0112 | 0.5981 | 17 | 0.0013889 | 22.5348 | 0.0112 | NA | NA | 0.95887 | 0.65366
318 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1540.9464 | 23.0381 | 61.1548 | 35.897 | 35 | 0.0112 | 2.4931 | 23.6854 | 0.0112 | 0.74794 | 17 | 0.0013889 | 23.6854 | 0.0112 | NA | NA | 0.87035 | 0.59171
319 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1845.7872 | 25.0246 | 66.5151 | 38.8361 | 35 | 0.0112 | 2.9947 | 24.6443 | 0.0112 | 0.89841 | 17 | 0.0013889 | 24.6443 | 0.0112 | NA | NA | 0.7966 | 0.54488
320 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1231.0866 | 20.7956 | 55.3964 | 32.7515 | 35 | 0.0085059 | 2 | 26.0881 | 0.0085059 | 0.6 | 17 | 0.0013889 | 26.0881 | 0.0085059 | NA | NA | 0.59413 | 0.38012
321 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.7159 | 20.7619 | 55.3293 | 32.7157 | 35 | 0.011284 | 2 | 26.562 | 0.011284 | 0.6 | 17 | 0.0013889 | 26.562 | 0.011284 | NA | NA | 0.64908 | 0.43684
322 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1219.2864 | 20.7207 | 55.2569 | 32.6777 | 35 | 0.01431 | 2 | 27.2563 | 0.01431 | 0.6 | 17 | 0.0013889 | 27.2563 | 0.01431 | NA | NA | 0.70398 | 0.50409
323 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1213.0691 | 20.6818 | 55.1781 | 32.6356 | 35 | 0.017611 | 2 | 27.8066 | 0.017611 | 0.6 | 17 | 0.0013889 | 27.8066 | 0.017611 | NA | NA | 0.79927 | 0.58947
324 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1206.0844 | 20.6377 | 55.0927 | 32.5902 | 35 | 0.021217 | 2 | 28.4828 | 0.021217 | 0.6 | 17 | 0.0013889 | 28.4828 | 0.021217 | NA | NA | 0.93102 | 0.7117
325 | PCC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1198.6145 | 20.5905 | 54.9998 | 32.5408 | 35 | 0.025161 | 2 | 29.1978 | 0.025161 | 0.6 | 17 | 0.0013889 | 29.1978 | 0.025161 | NA | NA | 1.1604 | 0.91287
326 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.0502 | 20.7564 | 55.3984 | 32.7572 | 35 | 0.0085059 | 2 | 27.4952 | 0.0085059 | 0.6 | 17 | 0.0013889 | 27.4952 | 0.0085059 | NA | NA | 0.50032 | 0.31813
327 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1220.2637 | 20.7194 | 55.3312 | 32.7218 | 35 | 0.011284 | 2 | 28.0962 | 0.011284 | 0.6 | 17 | 0.0013889 | 28.0962 | 0.011284 | NA | NA | 0.53106 | 0.36257
328 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1214.9162 | 20.6865 | 55.2582 | 32.6824 | 35 | 0.01431 | 2 | 28.4953 | 0.01431 | 0.6 | 17 | 0.0013889 | 28.4953 | 0.01431 | NA | NA | 0.59134 | 0.41696
329 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1208.8024 | 20.6483 | 55.1791 | 32.6401 | 35 | 0.017611 | 2 | 29.0258 | 0.017611 | 0.6 | 17 | 0.0013889 | 29.0258 | 0.017611 | NA | NA | 0.6638 | 0.48538
330 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1201.9455 | 20.605 | 55.0933 | 32.5944 | 35 | 0.021217 | 2 | 29.6761 | 0.021217 | 0.6 | 17 | 0.0013889 | 29.6761 | 0.021217 | NA | NA | 0.76055 | 0.58363
331 | PCP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1194.6715 | 20.5593 | 55.0001 | 32.5447 | 35 | 0.025161 | 2 | 30.3455 | 0.025161 | 0.6 | 17 | 0.0013889 | 30.3455 | 0.025161 | NA | NA | 0.9309 | 0.73333
332 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.2141 | 20.7498 | 55.3988 | 32.7582 | 35 | 0.0085059 | 2 | 27.7298 | 0.0085059 | 0.6 | 17 | 0.0013889 | 27.7298 | 0.0085059 | NA | NA | 0.48468 | 0.30585
333 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1219.5849 | 20.7141 | 55.3315 | 32.7225 | 35 | 0.011284 | 2 | 28.2879 | 0.011284 | 0.6 | 17 | 0.0013889 | 28.2879 | 0.011284 | NA | NA | 0.51631 | 0.34737
334 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1213.2839 | 20.6737 | 55.2586 | 32.6842 | 35 | 0.01431 | 2 | 28.9599 | 0.01431 | 0.6 | 17 | 0.0013889 | 28.9599 | 0.01431 | NA | NA | 0.5491 | 0.3924
335 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1207.1025 | 20.6349 | 55.1795 | 32.6419 | 35 | 0.017611 | 2 | 29.5135 | 0.017611 | 0.6 | 17 | 0.0013889 | 29.5135 | 0.017611 | NA | NA | 0.60961 | 0.44678
336 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1200.043 | 20.59 | 55.0936 | 32.5964 | 35 | 0.021217 | 2 | 30.2269 | 0.021217 | 0.6 | 17 | 0.0013889 | 30.2269 | 0.021217 | NA | NA | 0.68188 | 0.52047
337 | PPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1192.7079 | 20.5438 | 55.0002 | 32.5466 | 35 | 0.025161 | 2 | 30.9193 | 0.025161 | 0.6 | 17 | 0.0013889 | 30.9193 | 0.025161 | NA | NA | 0.81613 | 0.6386
338 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1227.7253 | 20.7694 | 55.3978 | 32.7553 | 35 | 0.0085059 | 2 | 27.0262 | 0.0085059 | 0.6 | 17 | 0.0013889 | 27.0262 | 0.0085059 | NA | NA | 0.53159 | 0.33801
339 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1222.3037 | 20.7353 | 55.3305 | 32.7195 | 35 | 0.011284 | 2 | 27.5209 | 0.011284 | 0.6 | 17 | 0.0013889 | 27.5209 | 0.011284 | NA | NA | 0.57532 | 0.38596
340 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1216.0063 | 20.695 | 55.2578 | 32.6812 | 35 | 0.01431 | 2 | 28.1855 | 0.01431 | 0.6 | 17 | 0.0013889 | 28.1855 | 0.01431 | NA | NA | 0.6195 | 0.44152
341 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1209.6538 | 20.655 | 55.1789 | 32.6392 | 35 | 0.017611 | 2 | 28.782 | 0.017611 | 0.6 | 17 | 0.0013889 | 28.782 | 0.017611 | NA | NA | 0.69089 | 0.51228
342 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1202.8986 | 20.6126 | 55.0932 | 32.5935 | 35 | 0.021217 | 2 | 29.4008 | 0.021217 | 0.6 | 17 | 0.0013889 | 29.4008 | 0.021217 | NA | NA | 0.79989 | 0.61111
343 | PPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1195.7647 | 20.568 | 55 | 32.5436 | 35 | 0.025161 | 2 | 30.0267 | 0.025161 | 0.6 | 17 | 0.0013889 | 30.0267 | 0.025161 | NA | NA | 0.99466 | 0.77602
344 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.2449 | 20.789 | 55.3968 | 32.7524 | 35 | 0.0085059 | 2 | 26.3226 | 0.0085059 | 0.6 | 17 | 0.0013889 | 26.3226 | 0.0085059 | NA | NA | 0.57849 | 0.3655
345 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1224.3492 | 20.7513 | 55.3298 | 32.7172 | 35 | 0.011284 | 2 | 26.9455 | 0.011284 | 0.6 | 17 | 0.0013889 | 26.9455 | 0.011284 | NA | NA | 0.61957 | 0.41988
346 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1218.1915 | 20.7121 | 55.2572 | 32.6789 | 35 | 0.01431 | 2 | 27.566 | 0.01431 | 0.6 | 17 | 0.0013889 | 27.566 | 0.01431 | NA | NA | 0.67582 | 0.48304
347 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1211.7865 | 20.6717 | 55.1784 | 32.637 | 35 | 0.017611 | 2 | 28.1724 | 0.017611 | 0.6 | 17 | 0.0013889 | 28.1724 | 0.017611 | NA | NA | 0.75863 | 0.56316
348 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1204.8084 | 20.6276 | 55.0929 | 32.5915 | 35 | 0.021217 | 2 | 28.85 | 0.021217 | 0.6 | 17 | 0.0013889 | 28.85 | 0.021217 | NA | NA | 0.87857 | 0.67427
349 | XPP | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1197.5171 | 20.5819 | 54.9999 | 32.5419 | 35 | 0.025161 | 2 | 29.5166 | 0.025161 | 0.6 | 17 | 0.0013889 | 29.5166 | 0.025161 | NA | NA | 1.0967 | 0.86374
350 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.0502 | 20.7564 | 55.3984 | 32.7572 | 35 | 0.0085059 | 2 | 27.4952 | 0.0085059 | 0.6 | 17 | 0.0013889 | 27.4952 | 0.0085059 | NA | NA | 0.50032 | 0.32281
351 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1220.9431 | 20.7247 | 55.331 | 32.721 | 35 | 0.011284 | 2 | 27.9044 | 0.011284 | 0.6 | 17 | 0.0013889 | 27.9044 | 0.011284 | NA | NA | 0.54582 | 0.36725
352 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1214.9162 | 20.6865 | 55.2582 | 32.6824 | 35 | 0.01431 | 2 | 28.4953 | 0.01431 | 0.6 | 17 | 0.0013889 | 28.4953 | 0.01431 | NA | NA | 0.59134 | 0.41871
353 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1208.3771 | 20.6449 | 55.1792 | 32.6405 | 35 | 0.017611 | 2 | 29.1477 | 0.017611 | 0.6 | 17 | 0.0013889 | 29.1477 | 0.017611 | NA | NA | 0.65025 | 0.48187
354 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1201.6281 | 20.6025 | 55.0934 | 32.5947 | 35 | 0.021217 | 2 | 29.7679 | 0.021217 | 0.6 | 17 | 0.0013889 | 29.7679 | 0.021217 | NA | NA | 0.74744 | 0.56608
355 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1201.6281 | 20.6025 | 55.0934 | 32.5947 | 35 | 0.021217 | 2 | 29.7679 | 0.021217 | 0.6 | 17 | 0.0013889 | 29.7679 | 0.021217 | NA | NA | 0.74744 | 0.56608
356 | XPC | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1194.2347 | 20.5559 | 55.0001 | 32.5451 | 35 | 0.025161 | 2 | 30.473 | 0.025161 | 0.6 | 17 | 0.0013889 | 30.473 | 0.025161 | NA | NA | 0.9054 | 0.70643
357 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1226.8873 | 20.7629 | 55.3981 | 32.7563 | 35 | 0.0085059 | 2 | 27.2607 | 0.0085059 | 0.6 | 17 | 0.0013889 | 27.2607 | 0.0085059 | NA | NA | 0.51595 | 0.32982
358 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1221.6231 | 20.73 | 55.3308 | 32.7203 | 35 | 0.011284 | 2 | 27.7126 | 0.011284 | 0.6 | 17 | 0.0013889 | 27.7126 | 0.011284 | NA | NA | 0.56057 | 0.37544
359 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1215.4611 | 20.6907 | 55.258 | 32.6818 | 35 | 0.01431 | 2 | 28.3404 | 0.01431 | 0.6 | 17 | 0.0013889 | 28.3404 | 0.01431 | NA | NA | 0.60542 | 0.42632
360 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1208.8024 | 20.6483 | 55.1791 | 32.6401 | 35 | 0.017611 | 2 | 29.0258 | 0.017611 | 0.6 | 17 | 0.0013889 | 29.0258 | 0.017611 | NA | NA | 0.6638 | 0.49123
361 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1201.9455 | 20.605 | 55.0933 | 32.5944 | 35 | 0.021217 | 2 | 29.6761 | 0.021217 | 0.6 | 17 | 0.0013889 | 29.6761 | 0.021217 | NA | NA | 0.76055 | 0.57953
362 | PCX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1194.453 | 20.5576 | 55.0001 | 32.5449 | 35 | 0.025161 | 2 | 30.4092 | 0.025161 | 0.6 | 17 | 0.0013889 | 30.4092 | 0.025161 | NA | NA | 0.91815 | 0.72339
363 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1230.2449 | 20.789 | 55.3968 | 32.7524 | 35 | 0.0085059 | 2 | 26.3226 | 0.0085059 | 0.6 | 17 | 0.0013889 | 26.3226 | 0.0085059 | NA | NA | 0.57849 | 0.37193
364 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1225.0322 | 20.7566 | 55.3296 | 32.7165 | 35 | 0.011284 | 2 | 26.7538 | 0.011284 | 0.6 | 17 | 0.0013889 | 26.7538 | 0.011284 | NA | NA | 0.63433 | 0.42515
365 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1218.7387 | 20.7164 | 55.257 | 32.6783 | 35 | 0.01431 | 2 | 27.4111 | 0.01431 | 0.6 | 17 | 0.0013889 | 27.4111 | 0.01431 | NA | NA | 0.6899 | 0.49123
366 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1212.6413 | 20.6784 | 55.1782 | 32.6361 | 35 | 0.017611 | 2 | 27.9285 | 0.017611 | 0.6 | 17 | 0.0013889 | 27.9285 | 0.017611 | NA | NA | 0.78572 | 0.57544
367 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1205.7652 | 20.6351 | 55.0927 | 32.5906 | 35 | 0.021217 | 2 | 28.5746 | 0.021217 | 0.6 | 17 | 0.0013889 | 28.5746 | 0.021217 | NA | NA | 0.91791 | 0.69649
368 | PPX | 0.5 | 0.005 | 0.5 | 1 | 0.3 | 1198.3949 | 20.5888 | 54.9998 | 32.541 | 35 | 0.025161 | 2 | 29.2616 | 0.025161 | 0.6 | 17 | 0.0013889 | 29.2616 | 0.025161 | NA | NA | 1.1477 | 0.90234