## Lin2018
Paper information
Authors | Lin et al.
Title | On the fundamental heat and mass transfer analysis of the counter-ﬂow dew point evaporative cooler
Year | 2018
Data type | Experimental data, extracted from graphs - Temperature profile
Description | Horizontal 4-channel counterflow D-IEC with an impervious polymer sheet to separate the dry and wet channels, and a piece of natural-fiber cellulose pasted on the wet channel side to absorb and retain water. Investigation of temperature and humidity of the primary air, secondary air, and water film by placing 8 RTD temperature sensor probes along the channels in each of the three flows. Evolution of the temperature and humidity profiles inside the exchanger provided for two sets of inlet conditions.
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Wet surface theory |  | counterflow |  | counterflow |  | parallel
Water recirculation | NA
Wall material | Polymer sheet + cellulose
Configuration | PCC
Geometry |  |  |  | Measurement uncertainties
Length | 0.8 | m |  | Temperature | 0.03 | K
Width | 0.18 | m |  | Humidity | 0.03 | K-wb
Height | 0.016 | m |  | Air flow | 2 | %
Channel height | 0.004 | m
Wall thickness | 0.00025 | m
Number of channels | 4 | -
Operating conditions
Primary fluid velocity | 2 | m/s
Secondary fluid velocity | 0.62 | m/s
Secondary-to-Primary flow rate ratio | 0.31 | kg/kg
Water supplied | NA | kg/s
| Tested conditions |  |  |  | Inlet conditions |  |  | Evolution along channel
Test | L | W | h_ch | SPR | T_pdi | w_pdi | v_pdi | x | T_pd | T_sw | w_sw | T_wf
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 78.7808 | 30.4638 | 27.2689 | 0.022643 | 28.1
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 179.1325 | 29.0261 | 26.1329 | 0.021293 | 26.9
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 280.4221 | 27.7275 | 24.9003 | 0.020156 | 25.6
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 380.7738 | 26.5681 | 23.7885 | 0.019144 | 24.5
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 481.1255 | 25.5246 | 22.7009 | 0.018267 | 23.4
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 581.4771 | 24.5507 | 21.855 | 0.017378 | 22.7
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 681.8289 | 23.4841 | 21.1299 | 0.016321 | 21.7
A | 0.8 | 0.18 | 0.004 | 0.32 | 32.6 | 0.014 | 2.1 | 781.2427 | 22.3246 | 21.1541 | 0.014841 | 20.4
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 77.4818 | 34.5946 | 29.5495 | 0.023573 | 30.7748
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 179.1767 | 32.2523 | 27.4595 | 0.0214 | 28.7928
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 277.9661 | 30.1622 | 25.5856 | 0.019459 | 26.5586
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 378.6925 | 28.1802 | 23.8198 | 0.017609 | 24.8649
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 479.4189 | 26.3423 | 22.2703 | 0.015853 | 23.0631
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 578.2082 | 24.6126 | 20.3964 | 0.014366 | 21.7658
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 678.9346 | 22.7748 | 19.4234 | 0.012369 | 19.2432
B | 0.8 | 0.18 | 0.004 | 0.31 | 38.2 | 0.0102 | 2 | 777.7241 | 20.8288 | 18.5586 | 0.010185 | 17.045