## Liu2019
Paper information
Authors | Liu et al.
Title | Experimental and numerical investigation of a high-eﬃciency dew-point evaporative cooler
Year | 2019
Data type | Experimental data, extracted from table
Description | D-IEC similar to a cooling tower to investigate the effect of water temperature and water flow rate on the primary air outlet temperature. Core of the exchanger made of 235 vertical aluminium plates, coated with a high-wettability porous fiber on the wet channel side, with water distribution in the wet channels by spraying. The temperature and water flow rate should be adjusted to optimise the performance of the D-IEC for large water-to-air flow rate ratios.
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Sprayed-water theory |  | counterflow |  | counterflow |  | parallel
Water recirculation | Yes
Wall material | Aluminium
Configuration | PCC
Geometry |  |  |  | Measurement uncertainties
Length | 1.05 | m |  | Temperature | 0.1 | K
Width | 0.716 | m |  | Humidity | 3.2441 | %
Height | 1.0062 | m |  | Air flow | 6.3 | %
Channel height | 0.0043 | m
Wall thickness | NA | m
Number of channels | 234 | -
Operating conditions
Primary fluid velocity | 1.6-2.5 | m/s
Secondary fluid velocity | 0.75-1 | m/s
Secondary-to-Primary flow rate ratio | 0.36-0.54 | kg/kg
Water supplied | 0.1 - 0.266 | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.403 | 1165.1947 | 8.23 | 28.0598 | 28.0598 | 38.3 | 0.010742 | 2.4314 | 23.4 | 0.010742 | 0.97985 | 26 | 0.0022792 | 23.4 | 0.010742 | NA | NA | 0.955 | 0.648
2 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.437 | 1084.2732 | 8.23 | 28.0375 | 28.0375 | 38.1 | 0.010454 | 2.2579 | 23 | 0.010454 | 0.98669 | 26 | 0.0022792 | 23 | 0.010454 | NA | NA | 0.962 | 0.651
3 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.437 | 1085.8546 | 8.23 | 28.0184 | 28.0184 | 38.1 | 0.010454 | 2.2579 | 22.5 | 0.010454 | 0.98669 | 26 | 0.0008547 | 22.5 | 0.010454 | NA | NA | 0.969 | 0.647
4 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.445 | 1104.1162 | 8.23 | 28.0043 | 28.0043 | 38.1 | 0.0099019 | 2.2918 | 22.1 | 0.0099019 | 1.0199 | 26 | 0.00091168 | 22.1 | 0.0099019 | NA | NA | 0.994 | 0.664
5 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.463 | 1054.1075 | 8.23 | 28.0255 | 28.0255 | 38.4 | 0.0090752 | 2.1893 | 22.3 | 0.0090752 | 1.0136 | 25.2 | 0.0020513 | 22.3 | 0.0090752 | NA | NA | 0.955 | 0.626
6 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.453 | 1037.42 | 8.23 | 28.0034 | 28.0034 | 38.4 | 0.0086882 | 2.1499 | 21.7 | 0.0086882 | 0.97392 | 25.2 | 0.0018234 | 21.7 | 0.0086882 | NA | NA | 0.977 | 0.635
7 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.455 | 1043.7654 | 8.23 | 27.9827 | 27.9827 | 38.8 | 0.0076524 | 2.1569 | 20.7 | 0.0076524 | 0.98137 | 24.4 | 0.0018234 | 20.7 | 0.0076524 | NA | NA | 0.996 | 0.633
8 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.437 | 1016.5697 | 8.23 | 27.9644 | 27.9644 | 38.6 | 0.0072666 | 2.0967 | 20.4 | 0.0072666 | 0.91626 | 24 | 0.0018234 | 20.4 | 0.0072666 | NA | NA | 0.963 | 0.593
9 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.381 | 1211.3178 | 8.23 | 27.9624 | 27.9624 | 37.6 | 0.0064299 | 2.4954 | 21.3 | 0.0064299 | 0.95074 | 24.5 | 0.0018234 | 21.3 | 0.0064299 | NA | NA | 0.892 | 0.544
10 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.536 | 913.4475 | 8.23 | 27.9275 | 27.9275 | 37.8 | 0.0065008 | 1.8769 | 20.2 | 0.0065008 | 1.006 | 23.9 | 0.0022792 | 20.2 | 0.0065008 | NA | NA | 0.959 | 0.587
11 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.461 | 830.3993 | 8.23 | 27.3316 | 27.3316 | 25.4 | 0.0058577 | 1.6286 | 17.2 | 0.0058577 | 0.7508 | 20 | 0.0022792 | 17.2 | 0.0058577 | NA | NA | 0.749 | 0.429
12 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.361 | 1169.9055 | 8.23 | 28.0973 | 28.0973 | 38.4 | 0.012536 | 2.4538 | 24.4 | 0.012536 | 0.8858 | 25 | 0.0022792 | 24.4 | 0.012536 | NA | NA | 0.966 | 0.714
13 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.462 | 1011.5655 | 8.23 | 28.0372 | 28.0372 | 38.6 | 0.01057 | 2.1067 | 22.5 | 0.01057 | 0.97331 | 25 | 0.0022792 | 22.5 | 0.01057 | NA | NA | 1.006 | 0.682
14 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.447 | 966.41 | 8.23 | 28.0368 | 28.0368 | 37.3 | 0.01393 | 2.0211 | 24 | 0.01393 | 0.90345 | 25 | 0.0022792 | 24 | 0.01393 | NA | NA | 1.039 | 0.739
15 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.395 | 1070.8177 | 8.23 | 28.0737 | 28.0737 | 38.3 | 0.014376 | 2.2471 | 24 | 0.014376 | 0.8876 | 25 | 0.0022792 | 24 | 0.014376 | NA | NA | 1.075 | 0.773
16 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.402 | 1167.5735 | 8.23 | 28.1412 | 28.1412 | 38.7 | 0.014697 | 2.4638 | 25.4 | 0.014697 | 0.99044 | 27 | 0.0022792 | 25.4 | 0.014697 | NA | NA | 0.993 | 0.715
17 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.391 | 1206.9405 | 8.23 | 28.0912 | 28.0912 | 37.6 | 0.013453 | 2.5332 | 25.1 | 0.013453 | 0.99047 | 27 | 0.0022792 | 25.1 | 0.013453 | NA | NA | 0.993 | 0.711