## Anisimov2014
Paper information
Authors | Anisimov et al.
Title | Numerical analysis of selected evaporative exchangers with the Maisotsenko cycle
Year | 2014
Data type | Numerical, extracted from graphs
Description | Numerical comparison of five EC configurations (cfr. Figure). Validation of D-IEC model against the experimental data of Riangvilaikul and Kumar (2010). The accuracy of the mathematical model prediction was considered to be similar for the perforated D-IEC and M-IEC. Validation of crossflow M-IECs against experimental data obtained with a test bench installed at Coolerado Manufacture, Denver, CO, USA. Testing of various combinations of operational parameters, data were reported for the primary channel only.
HEX characteristics
HEX type | M-IEC
Water injection type | Wet surface
Water recirculation | Yes
Wall material | NA
Configuration | Variable
Geometry
Length | 0.5 | m
Width | 0.5 | m
Height | 0.5 | m
Channel height | 0.004 | m
Wall thickness | 0.0005 | m
Number of channels | 125 | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 2-6 | m/s |  | V1 | 4 holes M-IEC |  | V4 | Crossflow/parallel M-IEC
Secondary fluid velocity | 0.7-6 | m/s |  | V2 | D-IEC |  | V5 | Crossflow/counterflow M-IEC
Secondary-to-Primary flow rate ratio | 0.3-2 | kg/kg |  | V3 | 4 holes D-IEC
Water supplied | NA | kg/s |  |  |  |  | 3002.4304 | 14.397 | 47.5424 | 62.9069
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_sdi | w_sdi | v_sdi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_wso | epsilon_wb | epsilon_dp
1 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1571.8918 | 4.12 | 13.3441 | 13.3441 | 25.0236 | 0.0059177 | 3 | NA | NA | 3 | NA | NA | 16.1432 | 0.0059177 | NA | NA | 0.83911 | 0.47338
2 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1528.6295 | 4.12 | 13.5048 | 13.5048 | 30.0236 | 0.0079551 | 3 | NA | NA | 3 | NA | NA | 19.6817 | 0.0079551 | NA | NA | 0.85818 | 0.53193
3 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1486.486 | 4.12 | 13.6623 | 13.6623 | 35 | 0.01059 | 3 | NA | NA | 3 | NA | NA | 23.1981 | 0.01059 | NA | NA | 0.87556 | 0.58606
4 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1445.3012 | 4.12 | 13.8154 | 13.8154 | 40 | 0.013971 | 3 | NA | NA | 3 | NA | NA | 26.6267 | 0.013971 | NA | NA | 0.89973 | 0.64325
5 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1403.9517 | 4.12 | 13.9674 | 13.9674 | 45 | 0.018279 | 3 | NA | NA | 3 | NA | NA | 30.2091 | 0.018279 | NA | NA | 0.90815 | 0.68595
6 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1566.0404 | 4.12 | 13.3676 | 13.3676 | 25.0472 | 0.0059177 | 3 | NA | NA | 0.9 | NA | NA | 17.352 | 0.0059177 | NA | NA | 0.71654 | 0.40424
7 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1524.9411 | 4.12 | 13.5202 | 13.5202 | 30 | 0.0079551 | 3 | NA | NA | 0.9 | NA | NA | 20.5168 | 0.0079551 | NA | NA | 0.79153 | 0.49062
8 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1482.1973 | 4.12 | 13.6808 | 13.6808 | 34.9764 | 0.01059 | 3 | NA | NA | 0.9 | NA | NA | 24.2091 | 0.01059 | NA | NA | 0.80136 | 0.5364
9 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1441.104 | 4.12 | 13.8341 | 13.8341 | 40 | 0.013971 | 3 | NA | NA | 0.9 | NA | NA | 27.6377 | 0.013971 | NA | NA | 0.83259 | 0.59525
10 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1400.3802 | 4.12 | 13.9839 | 13.9839 | 45 | 0.018279 | 3 | NA | NA | 0.9 | NA | NA | 31.1102 | 0.018279 | NA | NA | 0.85292 | 0.64424
11 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1564.6888 | 4.12 | 13.373 | 13.373 | 25.0472 | 0.0059177 | 3 | NA | NA | 0.9 | NA | NA | 17.6377 | 0.0059177 | NA | NA | 0.69769 | 0.3936
12 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1522.1612 | 4.12 | 13.5318 | 13.5318 | 29.9764 | 0.0079551 | 3 | NA | NA | 0.9 | NA | NA | 21.1542 | 0.0079551 | NA | NA | 0.7332 | 0.45446
13 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1479.7245 | 4.12 | 13.6915 | 13.6915 | 34.9764 | 0.01059 | 3 | NA | NA | 0.9 | NA | NA | 24.7806 | 0.01059 | NA | NA | 0.75684 | 0.5066
14 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1438.643 | 4.12 | 13.8452 | 13.8452 | 40.0236 | 0.013971 | 3 | NA | NA | 0.9 | NA | NA | 28.2091 | 0.013971 | NA | NA | 0.7923 | 0.56644
15 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1398.6497 | 4.12 | 13.992 | 13.992 | 44.9764 | 0.018279 | 3 | NA | NA | 0.9 | NA | NA | 31.5718 | 0.018279 | NA | NA | 0.82224 | 0.62107
16 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1566.2637 | 4.12 | 13.3667 | 13.3667 | 25 | 0.0059177 | 3 | NA | NA | 3 | NA | NA | 17.352 | 0.0059177 | NA | NA | 0.71654 | 0.40424
17 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1523.3402 | 4.12 | 13.5269 | 13.5269 | 30.0236 | 0.0079551 | 3 | NA | NA | 3 | NA | NA | 20.8465 | 0.0079551 | NA | NA | 0.76653 | 0.47512
18 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1480.9532 | 4.12 | 13.6862 | 13.6862 | 35 | 0.01059 | 3 | NA | NA | 3 | NA | NA | 24.4729 | 0.01059 | NA | NA | 0.7791 | 0.5215
19 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1440.2917 | 4.12 | 13.8378 | 13.8378 | 39.9764 | 0.013971 | 3 | NA | NA | 3 | NA | NA | 27.8575 | 0.013971 | NA | NA | 0.81245 | 0.58084
20 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1399.5304 | 4.12 | 13.9879 | 13.9879 | 44.9292 | 0.018279 | 3 | NA | NA | 3 | NA | NA | 31.3959 | 0.018279 | NA | NA | 0.83451 | 0.63034
21 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1563.8656 | 4.12 | 13.3763 | 13.3763 | 25.0236 | 0.0059177 | 3 | NA | NA | 3 | NA | NA | 17.8355 | 0.0059177 | NA | NA | 0.67883 | 0.38296
22 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1520.9765 | 4.12 | 13.5367 | 13.5367 | 29.9528 | 0.0079551 | 3 | NA | NA | 3 | NA | NA | 21.4399 | 0.0079551 | NA | NA | 0.71654 | 0.44414
23 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1477.8131 | 4.12 | 13.6998 | 13.6998 | 35.0236 | 0.01059 | 3 | NA | NA | 3 | NA | NA | 25.1762 | 0.01059 | NA | NA | 0.72716 | 0.48673
24 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1436.5774 | 4.12 | 13.8545 | 13.8545 | 39.9528 | 0.013971 | 3 | NA | NA | 3 | NA | NA | 28.7806 | 0.013971 | NA | NA | 0.75202 | 0.53764
25 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1395.5195 | 4.12 | 14.0065 | 14.0065 | 45.0236 | 0.018279 | 3 | NA | NA | 3 | NA | NA | 32.319 | 0.018279 | NA | NA | 0.77929 | 0.58862
26 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1528.7651 | 4.12 | 13.5043 | 13.5043 | 30 | 0.0079551 | 3 | NA | NA | 3 | NA | NA | 19.6755 | 0.0079551 | NA | NA | 0.85818 | 0.53193
27 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1522.6311 | 4.12 | 13.5193 | 13.5193 | 30 | 0.0093008 | 3 | NA | NA | 3 | NA | NA | 20.5303 | 0.0093008 | NA | NA | 0.86595 | 0.55504
28 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1510.6455 | 4.12 | 13.5483 | 13.5483 | 30 | 0.01201 | 3 | NA | NA | 3 | NA | NA | 22.1979 | 0.01201 | NA | NA | 0.87057 | 0.58954
29 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1499.1512 | 4.12 | 13.5754 | 13.5754 | 30 | 0.014742 | 3 | NA | NA | 3 | NA | NA | 23.781 | 0.014742 | NA | NA | 0.87249 | 0.61601
30 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1488.1329 | 4.12 | 13.6006 | 13.6006 | 30 | 0.017497 | 3 | NA | NA | 3 | NA | NA | 25.2797 | 0.017497 | NA | NA | 0.88211 | 0.64439
31 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1482.6146 | 4.12 | 13.6133 | 13.6133 | 30 | 0.018884 | 3 | NA | NA | 3 | NA | NA | 26.0396 | 0.018884 | NA | NA | 0.89123 | 0.66052
32 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1523.4449 | 4.12 | 13.5264 | 13.5264 | 30 | 0.0079551 | 3 | NA | NA | 0.9 | NA | NA | 20.847 | 0.0079551 | NA | NA | 0.76653 | 0.47512
33 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1517.8196 | 4.12 | 13.5394 | 13.5394 | 30 | 0.0093008 | 3 | NA | NA | 0.9 | NA | NA | 21.5963 | 0.0093008 | NA | NA | 0.76568 | 0.49077
34 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1507.3496 | 4.12 | 13.5621 | 13.5621 | 30 | 0.01201 | 3 | NA | NA | 0.9 | NA | NA | 22.9367 | 0.01201 | NA | NA | 0.79244 | 0.53663
35 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1496.3592 | 4.12 | 13.5872 | 13.5872 | 30 | 0.014742 | 3 | NA | NA | 0.9 | NA | NA | 24.4142 | 0.014742 | NA | NA | 0.78805 | 0.5564
36 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1486.3382 | 4.12 | 13.6083 | 13.6083 | 30 | 0.017497 | 3 | NA | NA | 0.9 | NA | NA | 25.6913 | 0.017497 | NA | NA | 0.80704 | 0.58955
37 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1481.1504 | 4.12 | 13.6196 | 13.6196 | 30 | 0.018884 | 3 | NA | NA | 0.9 | NA | NA | 26.3773 | 0.018884 | NA | NA | 0.80211 | 0.59447
38 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1522.7282 | 4.12 | 13.5294 | 13.5294 | 30 | 0.0079551 | 3 | NA | NA | 0.9 | NA | NA | 21.0053 | 0.0079551 | NA | NA | 0.74987 | 0.46479
39 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1517.2496 | 4.12 | 13.5418 | 13.5418 | 30 | 0.0093008 | 3 | NA | NA | 0.9 | NA | NA | 21.723 | 0.0093008 | NA | NA | 0.75657 | 0.48493
40 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1506.3161 | 4.12 | 13.5665 | 13.5665 | 30 | 0.01201 | 3 | NA | NA | 0.9 | NA | NA | 23.1689 | 0.01201 | NA | NA | 0.75896 | 0.51395
41 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1495.4768 | 4.12 | 13.5909 | 13.5909 | 30 | 0.014742 | 3 | NA | NA | 0.9 | NA | NA | 24.6148 | 0.014742 | NA | NA | 0.75991 | 0.53653
42 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1485.6029 | 4.12 | 13.6114 | 13.6114 | 30 | 0.017497 | 3 | NA | NA | 0.9 | NA | NA | 25.8602 | 0.017497 | NA | NA | 0.7695 | 0.56213
43 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1480.9218 | 4.12 | 13.6206 | 13.6206 | 30 | 0.018884 | 3 | NA | NA | 0.9 | NA | NA | 26.4301 | 0.018884 | NA | NA | 0.80211 | 0.59447
44 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1523.4449 | 4.12 | 13.5264 | 13.5264 | 30 | 0.0079551 | 3 | NA | NA | 3 | NA | NA | 20.847 | 0.0079551 | NA | NA | 0.76653 | 0.47512
45 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1517.8671 | 4.12 | 13.5392 | 13.5392 | 30 | 0.0093008 | 3 | NA | NA | 3 | NA | NA | 21.5858 | 0.0093008 | NA | NA | 0.76568 | 0.49077
46 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1507.1146 | 4.12 | 13.5631 | 13.5631 | 30 | 0.01201 | 3 | NA | NA | 3 | NA | NA | 22.9894 | 0.01201 | NA | NA | 0.78128 | 0.52907
47 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1496.3592 | 4.12 | 13.5872 | 13.5872 | 30 | 0.014742 | 3 | NA | NA | 3 | NA | NA | 24.4142 | 0.014742 | NA | NA | 0.78805 | 0.5564
48 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1486.3382 | 4.12 | 13.6083 | 13.6083 | 30 | 0.017497 | 3 | NA | NA | 3 | NA | NA | 25.6913 | 0.017497 | NA | NA | 0.80704 | 0.58955
49 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1481.1504 | 4.12 | 13.6196 | 13.6196 | 30 | 0.018884 | 3 | NA | NA | 3 | NA | NA | 26.3773 | 0.018884 | NA | NA | 0.80211 | 0.59447
50 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1520.6292 | 4.12 | 13.5382 | 13.5382 | 30 | 0.0079551 | 3 | NA | NA | 3 | NA | NA | 21.4697 | 0.0079551 | NA | NA | 0.70821 | 0.43897
51 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1515.3046 | 4.12 | 13.5499 | 13.5499 | 30 | 0.0093008 | 3 | NA | NA | 3 | NA | NA | 22.1557 | 0.0093008 | NA | NA | 0.71099 | 0.45571
52 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1504.9087 | 4.12 | 13.5724 | 13.5724 | 30 | 0.01201 | 3 | NA | NA | 3 | NA | NA | 23.4855 | 0.01201 | NA | NA | 0.72547 | 0.49128
53 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1494.6417 | 4.12 | 13.5945 | 13.5945 | 30 | 0.014742 | 3 | NA | NA | 3 | NA | NA | 24.8047 | 0.014742 | NA | NA | 0.73176 | 0.51666
54 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1485.0518 | 4.12 | 13.6137 | 13.6137 | 30 | 0.017497 | 3 | NA | NA | 3 | NA | NA | 25.9868 | 0.017497 | NA | NA | 0.75074 | 0.54842
55 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1480.2364 | 4.12 | 13.6235 | 13.6235 | 30 | 0.018884 | 3 | NA | NA | 3 | NA | NA | 26.5884 | 0.018884 | NA | NA | 0.75755 | 0.56144
56 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1009.5366 | 4.12 | 13.5257 | 13.5257 | 30 | 0.012 | 1.9977 | NA | NA | 1.9977 | NA | NA | 20.9944 | 0.012 | NA | NA | 1.0053 | 0.68086
57 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1512.9675 | 4.12 | 13.5484 | 13.5484 | 30 | 0.012 | 3.0046 | NA | NA | 3.0046 | NA | NA | 22.2022 | 0.012 | NA | NA | 0.87123 | 0.59008
58 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2013.14 | 4.12 | 13.57 | 13.57 | 30 | 0.012 | 4.0115 | NA | NA | 4.0115 | NA | NA | 23.3539 | 0.012 | NA | NA | 0.73719 | 0.4993
59 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2502.9927 | 11.5716 | 38.1571 | 38.1571 | 30 | 0.012 | 5 | NA | NA | 5 | NA | NA | 24.191 | 0.012 | NA | NA | 0.64784 | 0.43878
60 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1 | 3002.3581 | 14.3967 | 47.5248 | 47.5248 | 30 | 0.012 | 6.0115 | NA | NA | 6.0115 | NA | NA | 24.9831 | 0.012 | NA | NA | 0.55848 | 0.37826
61 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1009.969 | 4.12 | 13.5376 | 13.5376 | 30 | 0.012 | 2.0023 | NA | NA | 0.60069 | NA | NA | 21.6292 | 0.012 | NA | NA | 0.93824 | 0.63547
62 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1514.1951 | 4.12 | 13.5627 | 13.5627 | 30 | 0.012 | 3.0139 | NA | NA | 0.90416 | NA | NA | 22.9663 | 0.012 | NA | NA | 0.78187 | 0.52956
63 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 2007.458 | 4.12 | 13.5806 | 13.5806 | 30 | 0.012 | 4.0069 | NA | NA | 1.2021 | NA | NA | 23.9213 | 0.012 | NA | NA | 0.68134 | 0.46147
64 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 2504.0085 | 11.5775 | 38.2024 | 13.5948 | 30 | 0.012 | 5.0092 | NA | NA | 1.5028 | NA | NA | 24.6798 | 0.012 | NA | NA | 0.59199 | 0.40095
65 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 3002.4304 | 14.397 | 47.5424 | 13.6053 | 30 | 0.012 | 6.0162 | NA | NA | 1.8048 | NA | NA | 25.236 | 0.012 | NA | NA | 0.53614 | 0.36313
66 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1007.9055 | 4.12 | 13.5506 | 13.5506 | 30 | 0.012 | 2.0023 | NA | NA | 0.60069 | NA | NA | 22.3202 | 0.012 | NA | NA | 0.86006 | 0.58252
67 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 1502.4681 | 4.12 | 13.573 | 13.573 | 30 | 0.012 | 2.9954 | NA | NA | 0.89861 | NA | NA | 23.5169 | 0.012 | NA | NA | 0.72602 | 0.49173
68 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 2003.6498 | 4.12 | 13.5854 | 13.5854 | 30 | 0.012 | 4.0023 | NA | NA | 1.2007 | NA | NA | 24.1742 | 0.012 | NA | NA | 0.64784 | 0.43878
69 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 2500.9961 | 11.5596 | 38.1485 | 13.5966 | 30 | 0.012 | 5.0046 | NA | NA | 1.5014 | NA | NA | 24.7753 | 0.012 | NA | NA | 0.58082 | 0.39339
70 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.3 | 2997.5232 | 14.3703 | 47.4567 | 13.6059 | 30 | 0.012 | 6.0069 | NA | NA | 1.8021 | NA | NA | 25.2697 | 0.012 | NA | NA | 0.52497 | 0.35556
71 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1006.9188 | 4.12 | 13.5421 | 13.5421 | 30 | 0.012 | 1.9977 | NA | NA | 1.9977 | NA | NA | 21.8708 | 0.012 | NA | NA | 0.90474 | 0.61278
72 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1509.2031 | 4.12 | 13.5642 | 13.5642 | 30 | 0.012 | 3.0046 | NA | NA | 3.0046 | NA | NA | 23.0449 | 0.012 | NA | NA | 0.78187 | 0.52956
73 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2007.458 | 4.12 | 13.5806 | 13.5806 | 30 | 0.012 | 4.0069 | NA | NA | 4.0069 | NA | NA | 23.9213 | 0.012 | NA | NA | 0.68134 | 0.46147
74 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2504.5886 | 11.5809 | 38.2096 | 38.2096 | 30 | 0.012 | 5.0092 | NA | NA | 5.0092 | NA | NA | 24.6011 | 0.012 | NA | NA | 0.60316 | 0.40852
75 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1 | 3000.8196 | 14.3883 | 47.5085 | 47.5085 | 30 | 0.012 | 6.0115 | NA | NA | 6.0115 | NA | NA | 25.1573 | 0.012 | NA | NA | 0.53614 | 0.36313
76 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1008.9058 | 4.12 | 13.5589 | 13.5589 | 30 | 0.012 | 2.0069 | NA | NA | 2.0069 | NA | NA | 22.764 | 0.012 | NA | NA | 0.80421 | 0.54469
77 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 1502.4681 | 4.12 | 13.573 | 13.573 | 30 | 0.012 | 2.9954 | NA | NA | 2.9954 | NA | NA | 23.5169 | 0.012 | NA | NA | 0.72602 | 0.49173
78 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2003.3181 | 4.12 | 13.5864 | 13.5864 | 30 | 0.012 | 4.0023 | NA | NA | 4.0023 | NA | NA | 24.2303 | 0.012 | NA | NA | 0.64784 | 0.43878
79 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2502.8075 | 11.5703 | 38.1874 | 38.1874 | 30 | 0.012 | 5.0092 | NA | NA | 5.0092 | NA | NA | 24.8427 | 0.012 | NA | NA | 0.58082 | 0.39339
80 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1 | 2996.8297 | 14.3666 | 47.4493 | 47.4493 | 30 | 0.012 | 6.0069 | NA | NA | 6.0069 | NA | NA | 25.3483 | 0.012 | NA | NA | 0.52497 | 0.35556
81 | V1 | 0.5 | 0.004 | 0.5 | 1 | 0.25174 | 1511.6921 | 4.12 | 13.5541 | 13.5541 | 30 | 0.0107 | 3 | NA | NA | 0.75522 | NA | NA | 22.4459 | 0.0107 | NA | NA | 0.76441 | 0.50467
82 | V1 | 0.5 | 0.004 | 0.5 | 1 | 0.49536 | 1516.2372 | 4.12 | 13.5351 | 13.5351 | 30 | 0.0107 | 3 | NA | NA | 1.4861 | NA | NA | 21.4324 | 0.0107 | NA | NA | 0.86499 | 0.57107
83 | V1 | 0.5 | 0.004 | 0.5 | 1 | 0.90139 | 1518.0005 | 4.12 | 13.5277 | 13.5277 | 30 | 0.0107 | 3 | NA | NA | 2.7042 | NA | NA | 21.0405 | 0.0107 | NA | NA | 0.90522 | 0.59764
84 | V1 | 0.5 | 0.004 | 0.5 | 1 | 0.99652 | 1518.0614 | 4.12 | 13.5274 | 13.5274 | 30 | 0.0107 | 3 | NA | NA | 2.9896 | NA | NA | 21.027 | 0.0107 | NA | NA | 0.90522 | 0.59764
85 | V1 | 0.5 | 0.004 | 0.5 | 1 | 1.9942 | 1517.1488 | 4.12 | 13.5312 | 62.7488 | 30 | 0.0107 | 3 | NA | NA | 5.9826 | NA | NA | 21.2297 | 0.0107 | NA | NA | 0.8851 | 0.58436
86 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.24942 | 1510.3631 | 4.12 | 13.5597 | 13.5597 | 30 | 0.0107 | 3 | NA | NA | 0.74826 | NA | NA | 22.7432 | 0.0107 | NA | NA | 0.73423 | 0.48475
87 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.5 | 1517.088 | 4.12 | 13.5315 | 13.5315 | 30 | 0.0107 | 3 | NA | NA | 1.5 | NA | NA | 21.2432 | 0.0107 | NA | NA | 0.8851 | 0.58436
88 | V2 | 0.5 | 0.004 | 0.5 | 1 | 0.90139 | 1520.8043 | 4.12 | 13.516 | 13.516 | 30 | 0.0107 | 3 | NA | NA | 2.7042 | NA | NA | 20.4189 | 0.0107 | NA | NA | 0.96557 | 0.63748
89 | V2 | 0.5 | 0.004 | 0.5 | 1 | 1.0012 | 1521.1707 | 4.12 | 13.5145 | 13.5145 | 30 | 0.0107 | 3 | NA | NA | 3.0035 | NA | NA | 20.3378 | 0.0107 | NA | NA | 0.97563 | 0.64412
90 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.25174 | 1507.5301 | 4.12 | 13.5717 | 13.5717 | 30 | 0.0107 | 3 | NA | NA | 0.75522 | NA | NA | 23.3784 | 0.0107 | NA | NA | 0.66383 | 0.43827
91 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.5 | 1519.0967 | 4.12 | 13.5231 | 13.5231 | 30 | 0.0107 | 3 | NA | NA | 1.5 | NA | NA | 20.7973 | 0.0107 | NA | NA | 0.92534 | 0.61092
92 | V3 | 0.5 | 0.004 | 0.5 | 1 | 0.89907 | 1527.113 | 4.12 | 13.4898 | 13.4898 | 30 | 0.0107 | 3 | NA | NA | 2.6972 | NA | NA | 19.027 | 0.0107 | NA | NA | 1.1064 | 0.73044
93 | V3 | 0.5 | 0.004 | 0.5 | 1 | 1.0012 | 1527.9737 | 4.12 | 13.4862 | 13.4862 | 30 | 0.0107 | 3 | NA | NA | 3.0035 | NA | NA | 18.8378 | 0.0107 | NA | NA | 1.1265 | 0.74372
94 | V4 | 0.5 | 0.004 | 0.5 | 1 | 0.25406 | 1504.8257 | 4.12 | 13.5831 | 13.5831 | 30 | 0.0107 | 3 | NA | NA | 0.76218 | NA | NA | 23.9865 | 0.0107 | NA | NA | 0.60348 | 0.39842
95 | V4 | 0.5 | 0.004 | 0.5 | 1 | 0.50464 | 1510.182 | 4.12 | 13.5605 | 13.5605 | 30 | 0.0107 | 3 | NA | NA | 1.5139 | NA | NA | 22.7838 | 0.0107 | NA | NA | 0.72418 | 0.47811
96 | V4 | 0.5 | 0.004 | 0.5 | 1 | 0.90603 | 1512.5389 | 4.12 | 13.5506 | 13.5506 | 30 | 0.0107 | 3 | NA | NA | 2.7181 | NA | NA | 22.2568 | 0.0107 | NA | NA | 0.77447 | 0.51131
97 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1.0012 | 1512.7809 | 4.12 | 13.5496 | 13.5496 | 30 | 0.0107 | 3 | NA | NA | 3.0035 | NA | NA | 22.2027 | 0.0107 | NA | NA | 0.78452 | 0.51795
98 | V4 | 0.5 | 0.004 | 0.5 | 1 | 1.9988 | 1513.2047 | 4.12 | 13.5478 | 62.8688 | 30 | 0.0107 | 3 | NA | NA | 5.9965 | NA | NA | 22.1081 | 0.0107 | NA | NA | 0.79458 | 0.52459
99 | V5 | 0.5 | 0.004 | 0.5 | 1 | 0.2587 | 1502.2489 | 4.12 | 13.594 | 13.594 | 30 | 0.0107 | 3 | NA | NA | 0.7761 | NA | NA | 24.5676 | 0.0107 | NA | NA | 0.54313 | 0.35858
100 | V5 | 0.5 | 0.004 | 0.5 | 1 | 0.50232 | 1506.8082 | 4.12 | 13.5747 | 13.5747 | 30 | 0.0107 | 3 | NA | NA | 1.507 | NA | NA | 23.5405 | 0.0107 | NA | NA | 0.65377 | 0.43163
101 | V5 | 0.5 | 0.004 | 0.5 | 1 | 0.90371 | 1509.7596 | 4.12 | 13.5623 | 13.5623 | 30 | 0.0107 | 3 | NA | NA | 2.7111 | NA | NA | 22.8784 | 0.0107 | NA | NA | 0.71412 | 0.47147
102 | V5 | 0.5 | 0.004 | 0.5 | 1 | 1.0058 | 1509.9406 | 4.12 | 13.5615 | 13.5615 | 30 | 0.0107 | 3 | NA | NA | 3.0174 | NA | NA | 22.8378 | 0.0107 | NA | NA | 0.72418 | 0.47811
103 | V5 | 0.5 | 0.004 | 0.5 | 1 | 2.0012 | 1510.3631 | 4.12 | 13.5597 | 62.9069 | 30 | 0.0107 | 3 | NA | NA | 6.0035 | NA | NA | 22.7432 | 0.0107 | NA | NA | 0.73423 | 0.48475

## Anisimov2014_profiles
Paper information
Authors | Anisimov et al.
Title | Numerical analysis of selected evaporative exchangers with the Maisotsenko cycle
Year | 2014
Data type | Numerical, evolution profiles, extracted from graphs
Description | Numerical comparison of five EC configurations (cfr. Figure). Validation of D-IEC model against the experimental data of Riangvilaikul and Kumar (2010). The accuracy of the mathematical model prediction was considered to be similar for the perforated D-IEC and M-IEC. Validation of crossflow M-IECs against experimental data obtained with a test bench installed at Coolerado Manufacture, Denver, CO, USA. Evolution profile of the temperature for the primary and secondary air streams and the water film.
HEX characteristics
HEX type | M-IEC
Water injection type | Wet surface
Water recirculation | Yes
Wall material | NA
Configuration | Variable
Geometry
Length | 0.5 | m
Width | 0.5 | m
Height | 0.5 | m
Channel height | 0.004 | m
Wall thickness | 0.0005 | m
Number of channels | 125 | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 2-6 | m/s |  | V1 | 4 holes M-IEC |  | V4 | Crossflow/parallel M-IEC
Secondary fluid velocity | 0.7-6 | m/s |  | V2 | D-IEC |  | V5 | Crossflow/counterflow M-IEC
Secondary-to-Primary flow rate ratio | 0.3-2 | kg/kg |  | V3 | 4 holes D-IEC
Water supplied | NA | kg/s
| Testing conditions |  |  |  |  | Inlet conditions | [7 empty] | Profile evolution
Run | Test | L | W | h_ch | SPR | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | x_pd | T_pd | T_sw | w_ws | T_wf
1 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.00062118 | 29.9783 | 23.8478 | 0.013297 | 24.587
2 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.050932 | 29.413 | 23.7826 | 0.013095 | 24.2826
3 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.099379 | 28.8478 | 23.7391 | 0.012884 | 23.9565
4 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.14783 | 28.3696 | 23.7826 | 0.012674 | 23.6304
5 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.2 | 27.8478 | 23.9783 | 0.012384 | 23.2826
6 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.19814 | 27.8 | 22.8478 | 0.012822 | 23.587
7 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.25031 | 27.3913 | 22.7609 | 0.012692 | 23.3043
8 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.30248 | 26.9783 | 22.7174 | 0.012543 | 22.9783
9 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.3528 | 26.587 | 22.7826 | 0.012358 | 22.6087
10 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.40124 | 26.1522 | 22.9783 | 0.012104 | 22.3043
11 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.40124 | 26.2 | 21.9348 | 0.012545 | 22.6739
12 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.44969 | 25.7826 | 21.7826 | 0.012438 | 22.3478
13 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.50186 | 25.4348 | 21.7391 | 0.012315 | 22.0435
14 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.55031 | 25.0652 | 21.8261 | 0.01213 | 21.6957
15 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.60062 | 24.7174 | 22.0435 | 0.011902 | 21.3696
16 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.60248 | 24.7 | 21.0435 | 0.012299 | 21.8261
17 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.64907 | 24.3913 | 20.8261 | 0.012262 | 21.4783
18 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.70124 | 24.1087 | 20.6957 | 0.0122 | 21.087
19 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.74969 | 23.7609 | 20.7826 | 0.012025 | 20.7826
20 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.8 | 23.4565 | 21.0652 | 0.011787 | 20.3913
21 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.79627 | 23.5 | 20.2391 | 0.012139 | 21.0652
22 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.84845 | 23.1957 | 19.6957 | 0.012236 | 20.5435
23 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.90062 | 22.8913 | 19.2609 | 0.012289 | 20.0652
24 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 0.94907 | 22.5217 | 18.9783 | 0.012254 | 19.4783
25 | V1 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 19.3 | 0.012 | 3 | 18.8 | NA | 1.0012 | 22.2174 | 19.3478 | 0.011981 | 18.8478
26 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | -0.0036364 | 29.966 | 25.2681 | 0.023452 | 26.3404
27 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.098182 | 28.6638 | 24.3234 | 0.02209 | 25.3447
28 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.19818 | 27.5149 | 23.3787 | 0.020932 | 24.4255
29 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.3 | 26.3149 | 22.5106 | 0.019672 | 23.4809
30 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.39818 | 25.2936 | 21.7191 | 0.01862 | 22.5617
31 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.49818 | 24.3745 | 20.8 | 0.017757 | 21.6936
32 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.59818 | 23.4043 | 20.034 | 0.016762 | 20.9021
33 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.69455 | 22.4851 | 19.2426 | 0.015844 | 20.0596
34 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.79455 | 21.5404 | 18.5787 | 0.014839 | 19.1404
35 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.89455 | 20.6723 | 18.1191 | 0.013854 | 18.4
36 | V2 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 19.8 | 0.012 | 0.9 | 17.5 | NA | 0.99636 | 19.8043 | 19.8553 | 0.011978 | 17.5319
37 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | -0.0042552 | 29.953 | 25.7047 | 0.021004 | 26.8121
38 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.048936 | 29.3893 | 25.3423 | 0.020394 | 26.3691
39 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.095745 | 28.8255 | 25.1007 | 0.019736 | 25.8859
40 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.14468 | 28.3423 | 25.0201 | 0.019119 | 25.4228
41 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.19574 | 27.7785 | 25.302 | 0.018246 | 24.9799
42 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.19574 | 27.7785 | 24.6779 | 0.018501 | 25.5235
43 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.24894 | 27.3356 | 24.2953 | 0.018061 | 25.1007
44 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.29574 | 26.9128 | 24.0738 | 0.017583 | 24.6779
45 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.34468 | 26.5101 | 23.9732 | 0.017082 | 24.2349
46 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.39787 | 26.0268 | 24.3154 | 0.016293 | 23.8121
47 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.39787 | 26.0268 | 23.7718 | 0.016514 | 24.4564
48 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.44894 | 25.6846 | 23.4094 | 0.016201 | 24.0537
49 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.49574 | 25.3221 | 23.1074 | 0.015836 | 23.651
50 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.54894 | 25 | 22.9866 | 0.015451 | 23.1879
51 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.59574 | 24.5772 | 23.5705 | 0.014645 | 22.745
52 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.59787 | 24.5772 | 23.1074 | 0.014833 | 23.5705
53 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.64894 | 24.3356 | 22.7651 | 0.014647 | 23.1678
54 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.69787 | 24.0537 | 22.2617 | 0.014472 | 22.8054
55 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.74681 | 23.7517 | 22.0403 | 0.014155 | 22.2617
56 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.79574 | 23.3691 | 23.0671 | 0.013224 | 21.6577
57 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.79574 | 23.3691 | 22.745 | 0.013354 | 22.906
58 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.84468 | 23.2685 | 22.2617 | 0.013414 | 22.5839
59 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.90213 | 23.0067 | 21.557 | 0.013347 | 22
60 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.94681 | 22.7047 | 20.6107 | 0.013323 | 21.1141
61 | V3 | 0.5 | 0.5 | 0.004 | 0.3 | 30 | 0.012 | 3 | 22.2 | 0.012 | 0.9 | 19.8 | NA | 0.99787 | 22.2 | 22.2 | 0.012 | 19.7651
62 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | -0.0017698 | 30.0202 | 25.4343 | 0.012697 | 25.7576
63 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.10089 | 28.6263 | 24.6667 | 0.012444 | 24.8889
64 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.2 | 27.4949 | 23.9192 | 0.01229 | 24.1212
65 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.29735 | 26.5253 | 23.3131 | 0.012143 | 23.4545
66 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.4 | 25.5758 | 22.6869 | 0.012013 | 22.8081
67 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.50088 | 24.8687 | 22.202 | 0.011923 | 22.202
68 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.6 | 24.1414 | 21.6364 | 0.011858 | 21.6364
69 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.70265 | 23.5152 | 20.9293 | 0.01189 | 21.0909
70 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.8 | 22.9293 | 20.2424 | 0.011931 | 20.4646
71 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.90089 | 22.3434 | 19.7374 | 0.011898 | 19.7374
72 | V4 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 18.9 | 0.012 | 3 | 19.1 | NA | 0.99823 | 21.7576 | 18.8687 | 0.012013 | 19.0707
73 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | -0.0017698 | 29.9747 | 21.7046 | 0.015535 | 23.5949
74 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.10089 | 28.1013 | 21.9072 | 0.014695 | 23.0549
75 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.2 | 26.6835 | 21.9409 | 0.014108 | 22.6667
76 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.29735 | 25.4852 | 21.9747 | 0.013611 | 22.3291
77 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.4 | 24.6414 | 21.9578 | 0.013276 | 22.0928
78 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.50088 | 23.8987 | 22.0422 | 0.012942 | 21.8565
79 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.6 | 23.2911 | 22.1097 | 0.012669 | 21.7215
80 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.70265 | 22.9198 | 22.211 | 0.012478 | 21.6878
81 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.8 | 22.5316 | 22.2616 | 0.012301 | 21.654
82 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.90089 | 22.2447 | 22.4135 | 0.012124 | 21.6203
83 | V5 | 0.5 | 0.5 | 0.004 | 1 | 30 | 0.012 | 3 | 22.5 | 0.012 | 3 | 21.7 | NA | 0.99823 | 22.0253 | 22.5316 | 0.011987 | 21.6709