## Cui2014
Paper information
Authors | Cui et al.
Title | Studying the performance of an improved dew-point evaporative design for cooling application
Year | 2014
Data type | Numerical, extracted from graphs
Description | CFD model for an M-IEC validated for the D-IEC configuration only, using two data sources from the literature.Validation of the temperature profile of the air inside the primary channelbased on experimental results from Hsu et al. (1989). Comparison of the predicted outlet temperature of primary air to the measured temperature reported by Woods and Kozubal (2013). Numerical investigation of the effect of inlet air conditions and exchanger geometry on the performance of an M-IEC.
HEX characteristics |  |  | Configuration
HEX type | M-IEC |  | pd | sd | sd | sw
Water injection type | Wet surface |  | Parallel |  | Crossflow
Water recirculation | Yes
Wall material | NA
Configuration | PPX
Geometry
Length | 1 | m
Width | 1 | m
Height |  | m
Channel height | 0.006 | m
Wall thickness | 0.0002 | m
Number of channels |  | -
Operating conditions |  |  |  | Tests
Primary fluid velocity | 1-2.5 | m/s |  | A | Varied inlet conditions
Secondary fluid velocity | 1-2.5 | m/s |  | B | Varied HEX dimensions
Secondary-to-Primary flow rate ratio | 0.5 | kg/kg |  | C | Varied inlet air velocity
Water supplied | NA | kg/s
| Testing conditions | [10 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | h_ch_s | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_sdi | w_sdi | v_sdi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_wso | epsilon_wb | epsilon_dp
1 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 790.6024 | 17.0711 | 36.7146 | 54.442 | 25.0153 | 0.008 | 1 | 25.0153 | 0.008 | 2 | NA | NA | 13.4388 | 0.008 | NA | NA | 1.325 | 0.8049
2 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 777.1324 | 16.9396 | 36.7278 | 54.481 | 29.9694 | 0.008 | 1 | 29.9694 | 0.008 | 2 | NA | NA | 14.1647 | 0.008 | NA | NA | 1.3194 | 0.81779
3 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 764.0868 | 16.8112 | 36.7408 | 54.5199 | 34.9694 | 0.008 | 1 | 34.9694 | 0.008 | 2 | NA | NA | 14.8194 | 0.008 | NA | NA | 1.3119 | 0.82832
4 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 751.7447 | 16.6888 | 36.7536 | 54.5575 | 40 | 0.008 | 1 | 40 | 0.008 | 2 | NA | NA | 15.2841 | 0.008 | NA | NA | 1.3106 | 0.84172
5 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 776.6427 | 16.9442 | 36.6652 | 54.3876 | 25.0153 | 0.012 | 1 | 25.0153 | 0.012 | 2 | NA | NA | 17.8578 | 0.012 | NA | NA | 1.3 | 0.86774
6 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 763.8854 | 16.8185 | 36.6769 | 54.4239 | 29.9847 | 0.012 | 1 | 29.9847 | 0.012 | 2 | NA | NA | 18.4196 | 0.012 | NA | NA | 1.2925 | 0.87526
7 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 751.4047 | 16.6946 | 36.6887 | 54.4603 | 35 | 0.012 | 1 | 35 | 0.012 | 2 | NA | NA | 18.9621 | 0.012 | NA | NA | 1.2819 | 0.87972
8 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 739.5848 | 16.5764 | 36.7001 | 54.4957 | 40.0153 | 0.012 | 1 | 40.0153 | 0.012 | 2 | NA | NA | 19.3499 | 0.012 | NA | NA | 1.2794 | 0.88891
9 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 752.2578 | 16.7125 | 36.6241 | 54.3617 | 30 | 0.016 | 1 | 30 | 0.016 | 2 | NA | NA | 22.1079 | 0.016 | NA | NA | 1.26 | 0.90467
10 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 740.3921 | 16.5937 | 36.6345 | 54.3955 | 35 | 0.016 | 1 | 35 | 0.016 | 2 | NA | NA | 22.5197 | 0.016 | NA | NA | 1.2537 | 0.90939
11 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 728.8655 | 16.4775 | 36.6449 | 54.4292 | 40 | 0.016 | 1 | 40 | 0.016 | 2 | NA | NA | 22.9131 | 0.016 | NA | NA | 1.2462 | 0.91258
12 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 742.0648 | 16.6199 | 36.5696 | 54.2951 | 30 | 0.02 | 1 | 30 | 0.02 | 2 | NA | NA | 25.2822 | 0.02 | NA | NA | 1.2256 | 0.91782
13 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 730.6243 | 16.5046 | 36.5788 | 54.3268 | 35 | 0.02 | 1 | 35 | 0.02 | 2 | NA | NA | 25.6128 | 0.02 | NA | NA | 1.2263 | 0.92575
14 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 719.4546 | 16.3911 | 36.5881 | 54.3586 | 40 | 0.02 | 1 | 40 | 0.02 | 2 | NA | NA | 25.9494 | 0.02 | NA | NA | 1.22 | 0.92804
15 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 785.0365 | 17.0216 | 36.6887 | 54.4108 | 25.016 | 0.01 | 1 | 24.5 | 0.0096 | 2 | NA | NA | 15.0309 | 0.01 | NA | NA | 1.4127 | 0.90462
16 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 772.3883 | 16.8977 | 36.7006 | 54.447 | 30.0319 | 0.01 | 1 | 24.5 | 0.0096 | 2 | NA | NA | 15.4043 | 0.01 | NA | NA | 1.399 | 0.91108
17 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 760.1628 | 16.777 | 36.7124 | 54.4829 | 35.016 | 0.01 | 1 | 24.5 | 0.0096 | 2 | NA | NA | 15.7668 | 0.01 | NA | NA | 1.3833 | 0.91499
18 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 748.5715 | 16.6617 | 36.724 | 54.5178 | 40.0319 | 0.01 | 1 | 24.5 | 0.0096 | 2 | NA | NA | 15.95 | 0.01 | NA | NA | 1.3775 | 0.92428
19 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 783.3387 | 17.005 | 36.6902 | 54.4156 | 24.984 | 0.01 | 1 | 24.984 | 0.01 | 2 | NA | NA | 15.7781 | 0.01 | NA | NA | 1.3069 | 0.83682
20 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 770.1118 | 16.8753 | 36.7028 | 54.4537 | 29.984 | 0.01 | 1 | 29.984 | 0.01 | 2 | NA | NA | 16.4373 | 0.01 | NA | NA | 1.3 | 0.8466
21 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 757.3353 | 16.749 | 36.7152 | 54.4914 | 35.0319 | 0.01 | 1 | 35.0319 | 0.01 | 2 | NA | NA | 17.0072 | 0.01 | NA | NA | 1.2941 | 0.85598
22 | A | 1 | 0.006 | 0.003 | 1 | 1 | 1 | 745.3414 | 16.6295 | 36.7272 | 54.5277 | 40.0319 | 0.01 | 1 | 40.0319 | 0.01 | 2 | NA | NA | 17.4221 | 0.01 | NA | NA | 1.2931 | 0.86771
23 | B | 0.30128 | 0.006 | 0.003 | 1 | 1 | 1 | 749.2653 | 16.6687 | 36.7233 | 54.5157 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 25.667 | 0.01 | NA | NA | 0.41532 | 0.27047
24 | B | 0.49914 | 0.006 | 0.003 | 1 | 1 | 1 | 760.9231 | 16.7845 | 36.7117 | 54.4807 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 20.4462 | 0.01 | NA | NA | 0.91574 | 0.59636
25 | B | 0.79979 | 0.006 | 0.003 | 1 | 1 | 1 | 767.3505 | 16.8481 | 36.7054 | 54.4617 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 17.6227 | 0.01 | NA | NA | 1.1864 | 0.77261
26 | B | 0.99764 | 0.006 | 0.003 | 1 | 1 | 1 | 770.1262 | 16.8754 | 36.7028 | 54.4536 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 16.4151 | 0.01 | NA | NA | 1.3021 | 0.84798
27 | B | 1.1981 | 0.006 | 0.003 | 1 | 1 | 1 | 771.6433 | 16.8904 | 36.7013 | 54.4492 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 15.7581 | 0.01 | NA | NA | 1.3651 | 0.889
28 | B | 1.4961 | 0.006 | 0.003 | 1 | 1 | 1 | 773.3713 | 16.9074 | 36.6996 | 54.4442 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 15.0122 | 0.01 | NA | NA | 1.4366 | 0.93555
29 | B | 0.30514 | 0.01 | 0.005 | 1 | 1 | 1 | 1240.0791 | 20.8698 | 27.678 | 40.6963 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 28.0466 | 0.01 | NA | NA | 0.18723 | 0.12193
30 | B | 0.5 | 0.01 | 0.005 | 1 | 1 | 1 | 1250.409 | 20.9498 | 27.6761 | 40.6877 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 25.2231 | 0.01 | NA | NA | 0.45787 | 0.29818
31 | B | 0.79979 | 0.01 | 0.005 | 1 | 1 | 1 | 1264.7998 | 21.0606 | 27.6736 | 40.6758 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 21.3519 | 0.01 | NA | NA | 0.82894 | 0.53983
32 | B | 1.0011 | 0.01 | 0.005 | 1 | 1 | 1 | 1272.0287 | 21.1161 | 27.6723 | 40.6699 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 19.434 | 0.01 | NA | NA | 1.0128 | 0.65954
33 | B | 1.2002 | 0.01 | 0.005 | 1 | 1 | 1 | 1277.0205 | 21.1543 | 27.6715 | 40.6659 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 18.1199 | 0.01 | NA | NA | 1.1387 | 0.74157
34 | B | 1.4979 | 0.01 | 0.005 | 1 | 1 | 1 | 1281.6355 | 21.1895 | 27.6707 | 40.6622 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 16.9124 | 0.01 | NA | NA | 1.2545 | 0.81695
35 | B | 1.9946 | 0.01 | 0.005 | 1 | 1 | 1 | 1286.2091 | 21.2244 | 27.6699 | 40.6585 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 15.7226 | 0.01 | NA | NA | 1.3685 | 0.89122
36 | C | 1 | 0.01 | 0.005 | 1 | 1 | 1 | 1270.6336 | 21.1054 | 27.6726 | 40.671 | 30 | 0.01 | 1 | 30 | 0.01 | 2 | NA | NA | 19.8028 | 0.01 | NA | NA | 0.97742 | 0.63652
37 | C | 1 | 0.01 | 0.005 | 1 | 1 | 1 | 1887.022 | 25.2805 | 33.3024 | 48.64 | 30 | 0.01 | 1.5 | 30 | 0.01 | 3 | NA | NA | 23.1682 | 0.01 | NA | NA | 0.65484 | 0.42645
38 | C | 1 | 0.01 | 0.005 | 1 | 1 | 1 | 2496.2532 | 11.5292 | 15.244 | 55.353 | 30 | 0.01 | 2 | 30 | 0.01 | 4 | NA | NA | 25.8437 | 0.01 | NA | NA | 0.39839 | 0.25944
39 | C | 1 | 0.01 | 0.005 | 1 | 1 | 1 | 3106.4628 | 14.9532 | 19.8124 | 61.2632 | 30 | 0.01 | 2.5 | 30 | 0.01 | 5 | NA | NA | 27.3581 | 0.01 | NA | NA | 0.25323 | 0.16491