## Guzelel2024
Paper information
Authors | Guzelel et al.
Title | Performance evaluation of different types of indirect evaporative coolers: A CFD-based comparative study
Year | 2024
Data type | Numerical, extracted from graphs
Description | CFD model of various IEC configurations (cfr. Figure) validated against the experimental data of Riangvilaikul and Kumar (2010) for the D-IEC configuration only. Comparison of those five configurations in terms of dew point effectiveness, water consumption, and cooling capacity for variable operational conditions. Temperature at the primary outlet and the specific humidity at the secondary outlet deduced from the dew point effectiveness and water consumption, respectively. Temperature at the secondary outlet computed through an energy balance on the evaporative exchanger.
HEX characteristics
HEX type | Variable
Water injection type | Wet surface
Water recirculation | Yes
Wall material | Aluminium
Configuration | CF
Geometry
Length | 1 | m
Width |  | m
Height |  | m
Channel height | 0.0025 | m
Wall thickness | 0.0005 | m
Number of channels | NA | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 1-5 | m/s |  | T0 | Standard IEC |  | T3 | M-IEC
Secondary fluid velocity | 0.5-2.5 | m/s |  | T1 | D-IEC |  | T4 | 4 holes M-IEC
Secondary-to-Primary flow rate ratio | 0.2-0.8 | kg/kg |  | T2 | 4 holes D-IEC
Water supplied | NA | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_si | w_si | v_si | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_wso | epsilon_wb | epsilon_dp
1 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 952.2289 | 7.54 | 39.4238 | 39.4238 | 25 | 0.016 | 3 | 25 | 0.016 | 1.5 | NA | NA | 22.8625 | 0.016 | 24.9419 | 0.01776 | 0.79409 | 0.57422
2 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 932.6316 | 7.54 | 39.8082 | 39.8082 | 30 | 0.016 | 3 | 30 | 0.016 | 1.5 | NA | NA | 24.8966 | 0.016 | 29.7642 | 0.020226 | 0.81423 | 0.58489
3 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 913.9709 | 7.54 | 40.185 | 40.185 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 26.8206 | 0.016 | 34.4392 | 0.022825 | 0.82376 | 0.59556
4 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 896.2382 | 7.54 | 40.5533 | 40.5533 | 40 | 0.016 | 3 | 40 | 0.016 | 1.5 | NA | NA | 28.6159 | 0.016 | 38.9082 | 0.025594 | 0.83147 | 0.608
5 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 879.2962 | 7.54 | 40.9151 | 40.9151 | 45 | 0.016 | 3 | 45 | 0.016 | 1.5 | NA | NA | 30.315 | 0.016 | 43.2921 | 0.028458 | 0.83871 | 0.61867
6 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 952.8729 | 7.54 | 39.4114 | 39.4114 | 25 | 0.016 | 3 | 22.6354 | 0.016 | 1.5 | NA | NA | 22.6354 | 0.016 | 22.8011 | 0.017856 | 0.90753 | 0.63467
7 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 934.0434 | 7.54 | 39.7801 | 39.7801 | 30 | 0.016 | 3 | 24.3819 | 0.016 | 1.5 | NA | NA | 24.3819 | 0.016 | 24.7604 | 0.02041 | 0.89406 | 0.64356
8 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 916.1583 | 7.54 | 40.1402 | 40.1402 | 35 | 0.016 | 3 | 25.9972 | 0.016 | 1.5 | NA | NA | 25.9972 | 0.016 | 26.4591 | 0.023117 | 0.90413 | 0.656
9 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 899.0829 | 7.54 | 40.4936 | 40.4936 | 40 | 0.016 | 3 | 27.5112 | 0.016 | 1.5 | NA | NA | 27.5112 | 0.016 | 27.9754 | 0.025934 | 0.9117 | 0.66667
10 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 882.5551 | 7.54 | 40.8447 | 40.8447 | 45 | 0.016 | 3 | 29.0102 | 0.016 | 1.5 | NA | NA | 29.0102 | 0.016 | 29.246 | 0.028853 | 0.91289 | 0.67378
11 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 953.1159 | 7.54 | 39.4067 | 39.4067 | 25 | 0.016 | 3 | 22.5498 | 0.016 | 1.5 | NA | NA | 22.5498 | 0.016 | 22.889 | 0.017855 | 0.94535 | 0.65778
12 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 934.6666 | 7.54 | 39.7677 | 39.7677 | 30 | 0.016 | 3 | 24.1551 | 0.016 | 1.5 | NA | NA | 24.1551 | 0.016 | 24.9184 | 0.020438 | 0.92599 | 0.67022
13 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.2552 | 7.54 | 40.1179 | 40.1179 | 35 | 0.016 | 3 | 25.5855 | 0.016 | 1.5 | NA | NA | 25.5855 | 0.016 | 26.6798 | 0.023194 | 0.94431 | 0.68622
14 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 900.3411 | 7.54 | 40.4672 | 40.4672 | 40 | 0.016 | 3 | 27.0244 | 0.016 | 1.5 | NA | NA | 27.0244 | 0.016 | 28.3255 | 0.025987 | 0.94817 | 0.69333
15 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 884.2218 | 7.54 | 40.8089 | 40.8089 | 45 | 0.016 | 3 | 28.3459 | 0.016 | 1.5 | NA | NA | 28.3459 | 0.016 | 29.8104 | 0.028888 | 0.95282 | 0.70222
16 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 953.3801 | 7.54 | 39.4016 | 39.4016 | 25 | 0.016 | 3 | 25 | 0.016 | 1.5 | NA | NA | 22.4567 | 0.016 | 25.2569 | 0.017961 | 0.94535 | 0.68267
17 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 935.3866 | 7.54 | 39.7534 | 39.7534 | 30 | 0.016 | 3 | 30 | 0.016 | 1.5 | NA | NA | 23.8934 | 0.016 | 30.4893 | 0.020743 | 0.97389 | 0.70044
18 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 918.0609 | 7.54 | 40.1015 | 40.1015 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.2836 | 0.016 | 35.527 | 0.023621 | 0.97445 | 0.70756
19 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 901.6507 | 7.54 | 40.4398 | 40.4398 | 40 | 0.016 | 3 | 40 | 0.016 | 1.5 | NA | NA | 26.5189 | 0.016 | 40.269 | 0.026723 | 0.98464 | 0.72
20 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 885.5349 | 7.54 | 40.7807 | 40.7807 | 45 | 0.016 | 3 | 45 | 0.016 | 1.5 | NA | NA | 27.824 | 0.016 | 44.9319 | 0.029782 | 0.98135 | 0.72356
21 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 953.1159 | 7.54 | 39.4067 | 39.4067 | 25 | 0.016 | 3 | 25 | 0.016 | 1.5 | NA | NA | 22.5498 | 0.016 | 25.1051 | 0.017947 | 0.94535 | 0.65778
22 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 934.6666 | 7.54 | 39.7677 | 39.7677 | 30 | 0.016 | 3 | 30 | 0.016 | 1.5 | NA | NA | 24.1551 | 0.016 | 30.1591 | 0.020666 | 0.92599 | 0.67022
23 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.2552 | 7.54 | 40.1179 | 40.1179 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.5855 | 0.016 | 34.9972 | 0.023594 | 0.94431 | 0.68622
24 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 900.3411 | 7.54 | 40.4672 | 40.4672 | 40 | 0.016 | 3 | 40 | 0.016 | 1.5 | NA | NA | 27.0244 | 0.016 | 39.6408 | 0.026574 | 0.94817 | 0.69333
25 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 884.2218 | 7.54 | 40.8089 | 40.8089 | 45 | 0.016 | 3 | 45 | 0.016 | 1.5 | NA | NA | 28.3459 | 0.016 | 44.0572 | 0.029723 | 0.95282 | 0.70222
26 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 938.5455 | 7.54 | 39.9223 | 39.9223 | 35 | 0.006 | 3 | 35 | 0.006 | 1.5 | NA | NA | 21.4342 | 0.006 | 34.8811 | 0.016796 | 0.8019 | 0.47534
27 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 925.7175 | 7.54 | 40.0631 | 40.0631 | 35 | 0.011 | 3 | 35 | 0.011 | 1.5 | NA | NA | 24.2765 | 0.011 | 34.5626 | 0.019749 | 0.81079 | 0.54798
28 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 914.0437 | 7.54 | 40.1835 | 40.1835 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 26.7932 | 0.016 | 34.4423 | 0.022846 | 0.82376 | 0.59776
29 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 903.2051 | 7.54 | 40.2895 | 40.2895 | 35 | 0.021 | 3 | 35 | 0.021 | 1.5 | NA | NA | 29.0836 | 0.021 | 34.4462 | 0.026041 | 0.82919 | 0.63274
30 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 893.1833 | 7.54 | 40.381 | 40.381 | 35 | 0.026 | 3 | 35 | 0.026 | 1.5 | NA | NA | 31.1392 | 0.026 | 34.526 | 0.029364 | 0.84838 | 0.66233
31 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 944.3383 | 7.54 | 39.8068 | 39.8068 | 35 | 0.006 | 3 | 19.3493 | 0.006 | 1.5 | NA | NA | 19.3493 | 0.006 | 21.4724 | 0.01767 | 0.92572 | 0.54798
32 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 929.0091 | 7.54 | 39.9965 | 39.9965 | 35 | 0.011 | 3 | 23.0632 | 0.011 | 1.5 | NA | NA | 23.0632 | 0.011 | 24.1537 | 0.020177 | 0.90171 | 0.60987
33 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 916.2313 | 7.54 | 40.1388 | 40.1388 | 35 | 0.016 | 3 | 25.9698 | 0.016 | 1.5 | NA | NA | 25.9698 | 0.016 | 26.4442 | 0.023135 | 0.90413 | 0.6583
34 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 904.6176 | 7.54 | 40.2603 | 40.2603 | 35 | 0.021 | 3 | 28.5415 | 0.021 | 1.5 | NA | NA | 28.5415 | 0.021 | 28.6739 | 0.026224 | 0.91352 | 0.69058
35 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 893.9443 | 7.54 | 40.3652 | 40.3652 | 35 | 0.026 | 3 | 30.8417 | 0.026 | 1.5 | NA | NA | 30.8417 | 0.026 | 30.7377 | 0.029466 | 0.91364 | 0.71345
36 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 944.3383 | 7.54 | 39.8068 | 39.8068 | 35 | 0.006 | 3 | 19.3493 | 0.006 | 1.5 | NA | NA | 19.3493 | 0.006 | 22.0178 | 0.017448 | 0.92572 | 0.54798
37 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 929.8616 | 7.54 | 39.9793 | 39.9793 | 35 | 0.011 | 3 | 22.7501 | 0.011 | 1.5 | NA | NA | 22.7501 | 0.011 | 24.5282 | 0.020149 | 0.92445 | 0.62601
38 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.2186 | 7.54 | 40.1186 | 40.1186 | 35 | 0.016 | 3 | 25.5992 | 0.016 | 1.5 | NA | NA | 25.5992 | 0.016 | 26.697 | 0.023181 | 0.94431 | 0.6852
39 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 905.4228 | 7.54 | 40.2437 | 40.2437 | 35 | 0.021 | 3 | 28.233 | 0.021 | 1.5 | NA | NA | 28.233 | 0.021 | 28.8311 | 0.026285 | 0.95568 | 0.72422
40 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 894.4523 | 7.54 | 40.3546 | 40.3546 | 35 | 0.026 | 3 | 30.6435 | 0.026 | 1.5 | NA | NA | 30.6435 | 0.026 | 30.8974 | 0.029481 | 0.95714 | 0.74709
41 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 947.0561 | 7.54 | 39.753 | 39.753 | 35 | 0.006 | 3 | 35 | 0.006 | 1.5 | NA | NA | 18.3783 | 0.006 | 36.2998 | 0.018642 | 0.97879 | 0.58161
42 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 931.7309 | 7.54 | 39.9417 | 39.9417 | 35 | 0.011 | 3 | 35 | 0.011 | 1.5 | NA | NA | 22.0652 | 0.011 | 35.5165 | 0.021129 | 0.97749 | 0.66099
43 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 918.0975 | 7.54 | 40.1007 | 40.1007 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.2698 | 0.016 | 35.0455 | 0.023828 | 0.97445 | 0.70942
44 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 905.9114 | 7.54 | 40.2337 | 40.2337 | 35 | 0.021 | 3 | 35 | 0.021 | 1.5 | NA | NA | 28.0461 | 0.021 | 34.7854 | 0.026746 | 0.98379 | 0.74439
45 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 894.7363 | 7.54 | 40.3487 | 40.3487 | 35 | 0.026 | 3 | 35 | 0.026 | 1.5 | NA | NA | 30.5326 | 0.026 | 34.6947 | 0.029792 | 0.9789 | 0.76592
46 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 944.3383 | 7.54 | 39.8068 | 39.8068 | 35 | 0.006 | 3 | 35 | 0.006 | 1.5 | NA | NA | 19.3493 | 0.006 | 37.3539 | 0.017448 | 0.92572 | 0.54798
47 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 929.8616 | 7.54 | 39.9793 | 39.9793 | 35 | 0.011 | 3 | 35 | 0.011 | 1.5 | NA | NA | 22.7501 | 0.011 | 36.2522 | 0.020283 | 0.92445 | 0.62601
48 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.2186 | 7.54 | 40.1186 | 40.1186 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.5992 | 0.016 | 35.5041 | 0.023375 | 0.94431 | 0.6852
49 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 905.4228 | 7.54 | 40.2437 | 40.2437 | 35 | 0.021 | 3 | 35 | 0.021 | 1.5 | NA | NA | 28.233 | 0.021 | 35.0776 | 0.026473 | 0.95568 | 0.72422
50 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 894.4523 | 7.54 | 40.3546 | 40.3546 | 35 | 0.026 | 3 | 35 | 0.026 | 1.5 | NA | NA | 30.6435 | 0.026 | 34.8725 | 0.029628 | 0.95714 | 0.74709
51 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 306.0447 | 7.54 | 40.1 | 40.1 | 35 | 0.016 | 1 | 35 | 0.016 | 0.5 | NA | NA | 25.2561 | 0.016 | 35.5238 | 0.023644 | 0.97445 | 0.70968
52 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 610.8209 | 7.54 | 40.1388 | 40.1388 | 35 | 0.016 | 2 | 35 | 0.016 | 1 | NA | NA | 25.9698 | 0.016 | 34.8477 | 0.023345 | 0.90413 | 0.65806
53 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 914.1893 | 7.54 | 40.1805 | 40.1805 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 26.7383 | 0.016 | 34.4516 | 0.022887 | 0.83381 | 0.60161
54 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 1216.2545 | 7.54 | 40.2215 | 40.2215 | 35 | 0.016 | 4 | 35 | 0.016 | 2 | NA | NA | 27.4931 | 0.016 | 34.2002 | 0.02238 | 0.75344 | 0.54677
55 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 1518.1444 | 7.54 | 40.2483 | 40.2483 | 35 | 0.016 | 5 | 35 | 0.016 | 2.5 | NA | NA | 27.9871 | 0.016 | 34.1033 | 0.022021 | 0.70321 | 0.51129
56 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 308.7024 | 7.54 | 39.9387 | 39.9387 | 35 | 0.016 | 1 | 22.2918 | 0.016 | 0.5 | NA | NA | 22.2918 | 0.016 | 39.6563 | 0.024344 | 1.2758 | 0.92581
57 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 613.7057 | 7.54 | 40.0507 | 40.0507 | 35 | 0.016 | 2 | 24.3503 | 0.016 | 1 | NA | NA | 24.3503 | 0.016 | 37.3525 | 0.023627 | 1.0649 | 0.77581
58 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 916.414 | 7.54 | 40.135 | 40.135 | 35 | 0.016 | 3 | 25.9011 | 0.016 | 1.5 | NA | NA | 25.9011 | 0.016 | 35.511 | 0.023129 | 0.91417 | 0.6629
59 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 1217.3192 | 7.54 | 40.2051 | 40.2051 | 35 | 0.016 | 4 | 27.1912 | 0.016 | 2 | NA | NA | 27.1912 | 0.016 | 33.966 | 0.022719 | 0.78358 | 0.56935
60 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 1517.1196 | 7.54 | 40.261 | 40.261 | 35 | 0.016 | 5 | 28.2205 | 0.016 | 2.5 | NA | NA | 28.2205 | 0.016 | 32.854 | 0.022342 | 0.68312 | 0.49355
61 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 308.1951 | 7.54 | 39.9693 | 39.9693 | 35 | 0.016 | 1 | 22.8545 | 0.016 | 0.5 | NA | NA | 22.8545 | 0.016 | 38.8799 | 0.024208 | 1.2155 | 0.88548
62 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 613.7793 | 7.54 | 40.0485 | 40.0485 | 35 | 0.016 | 2 | 24.3092 | 0.016 | 1 | NA | NA | 24.3092 | 0.016 | 37.3615 | 0.023657 | 1.0749 | 0.77903
63 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.1088 | 7.54 | 40.1209 | 40.1209 | 35 | 0.016 | 3 | 25.6404 | 0.016 | 1.5 | NA | NA | 25.6404 | 0.016 | 35.9887 | 0.023144 | 0.94431 | 0.68226
64 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 1219.2103 | 7.54 | 40.176 | 40.176 | 35 | 0.016 | 4 | 26.6559 | 0.016 | 2 | NA | NA | 26.6559 | 0.016 | 34.8591 | 0.022787 | 0.83381 | 0.60806
65 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 1520.3181 | 7.54 | 40.2215 | 40.2215 | 35 | 0.016 | 5 | 27.4931 | 0.016 | 2.5 | NA | NA | 27.4931 | 0.016 | 33.8639 | 0.022517 | 0.75344 | 0.54677
66 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 308.8139 | 7.54 | 39.932 | 39.932 | 35 | 0.016 | 1 | 35 | 0.016 | 0.5 | NA | NA | 22.1683 | 0.016 | 39.3983 | 0.024548 | 1.2859 | 0.93548
67 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 614.5656 | 7.54 | 40.0246 | 40.0246 | 35 | 0.016 | 2 | 35 | 0.016 | 1 | NA | NA | 23.87 | 0.016 | 37.1949 | 0.024078 | 1.1151 | 0.81129
68 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 918.0609 | 7.54 | 40.1015 | 40.1015 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.2836 | 0.016 | 35.5453 | 0.023613 | 0.97445 | 0.70806
69 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 1220.6196 | 7.54 | 40.1544 | 40.1544 | 35 | 0.016 | 4 | 35 | 0.016 | 2 | NA | NA | 26.258 | 0.016 | 34.2966 | 0.023337 | 0.87399 | 0.6371
70 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 1521.9517 | 7.54 | 40.2014 | 40.2014 | 35 | 0.016 | 5 | 35 | 0.016 | 2.5 | NA | NA | 27.1225 | 0.016 | 33.419 | 0.022998 | 0.79362 | 0.57419
71 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 307.9851 | 7.54 | 39.982 | 39.982 | 35 | 0.016 | 1 | 35 | 0.016 | 0.5 | NA | NA | 23.0878 | 0.016 | 38.0482 | 0.02436 | 1.1955 | 0.86774
72 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 613.7793 | 7.54 | 40.0485 | 40.0485 | 35 | 0.016 | 2 | 35 | 0.016 | 1 | NA | NA | 24.3092 | 0.016 | 36.3287 | 0.024078 | 1.0749 | 0.77903
73 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.548 | 7.54 | 40.1119 | 40.1119 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.4757 | 0.016 | 35.0412 | 0.023664 | 0.95436 | 0.69355
74 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 1219.9875 | 7.54 | 40.1641 | 40.1641 | 35 | 0.016 | 4 | 35 | 0.016 | 2 | NA | NA | 26.4364 | 0.016 | 34.089 | 0.023278 | 0.86394 | 0.62419
75 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 1521.9517 | 7.54 | 40.2014 | 40.2014 | 35 | 0.016 | 5 | 35 | 0.016 | 2.5 | NA | NA | 27.1225 | 0.016 | 33.419 | 0.022998 | 0.79362 | 0.57419
76 | T0 | 1 | 0.0025 | 1 | 1 | 0.2 | 910.9836 | 7.54 | 40.2463 | 40.2463 | 35 | 0.016 | 3 | 35 | 0.016 | 0.6 | NA | NA | 27.9504 | 0.016 | 32.5818 | 0.031214 | 0.70321 | 0.51368
77 | T0 | 1 | 0.0025 | 1 | 1 | 0.35 | 913.5833 | 7.54 | 40.1929 | 40.1929 | 35 | 0.016 | 3 | 35 | 0.016 | 1.05 | NA | NA | 26.9669 | 0.016 | 37.1267 | 0.024385 | 0.80367 | 0.58534
78 | T0 | 1 | 0.0025 | 1 | 1 | 0.5 | 913.9624 | 7.54 | 40.1852 | 40.1852 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 26.8238 | 0.016 | 34.6049 | 0.022755 | 0.82376 | 0.59577
79 | T0 | 1 | 0.0025 | 1 | 1 | 0.65 | 914.1995 | 7.54 | 40.1803 | 40.1803 | 35 | 0.016 | 3 | 35 | 0.016 | 1.95 | NA | NA | 26.7344 | 0.016 | 35.3068 | 0.021003 | 0.83381 | 0.60228
80 | T0 | 1 | 0.0025 | 1 | 1 | 0.8 | 914.0572 | 7.54 | 40.1832 | 40.1832 | 35 | 0.016 | 3 | 35 | 0.016 | 2.4 | NA | NA | 26.7881 | 0.016 | 36.7843 | 0.019415 | 0.82376 | 0.59837
81 | T1 | 1 | 0.0025 | 1 | 1 | 0.2 | 911.9276 | 7.54 | 40.2269 | 40.2269 | 35 | 0.016 | 3 | 27.5927 | 0.016 | 0.6 | NA | NA | 27.5927 | 0.016 | 28.8572 | 0.030487 | 0.74339 | 0.53974
82 | T1 | 1 | 0.0025 | 1 | 1 | 0.35 | 914.9113 | 7.54 | 40.1657 | 40.1657 | 35 | 0.016 | 3 | 26.4662 | 0.016 | 1.05 | NA | NA | 26.4662 | 0.016 | 27.125 | 0.02562 | 0.8539 | 0.62182
83 | T1 | 1 | 0.0025 | 1 | 1 | 0.5 | 916.1949 | 7.54 | 40.1395 | 40.1395 | 35 | 0.016 | 3 | 25.9834 | 0.016 | 1.5 | NA | NA | 25.9834 | 0.016 | 27.1452 | 0.022841 | 0.90413 | 0.657
84 | T1 | 1 | 0.0025 | 1 | 1 | 0.65 | 916.7664 | 7.54 | 40.1278 | 40.1278 | 35 | 0.016 | 3 | 25.7689 | 0.016 | 1.95 | NA | NA | 25.7689 | 0.016 | 25.5196 | 0.021867 | 0.92422 | 0.67264
85 | T1 | 1 | 0.0025 | 1 | 1 | 0.8 | 917.3861 | 7.54 | 40.1152 | 40.1152 | 35 | 0.016 | 3 | 25.5364 | 0.016 | 2.4 | NA | NA | 25.5364 | 0.016 | 25.0869 | 0.020986 | 0.95436 | 0.68958
86 | T2 | 1 | 0.0025 | 1 | 1 | 0.2 | 906.6619 | 7.54 | 40.3356 | 40.3356 | 35 | 0.016 | 3 | 29.5954 | 0.016 | 0.6 | NA | NA | 29.5954 | 0.016 | 28.4266 | 0.027421 | 0.54248 | 0.39381
87 | T2 | 1 | 0.0025 | 1 | 1 | 0.35 | 913.5833 | 7.54 | 40.1929 | 40.1929 | 35 | 0.016 | 3 | 26.9669 | 0.016 | 1.05 | NA | NA | 26.9669 | 0.016 | 27.7834 | 0.024972 | 0.80367 | 0.58534
88 | T2 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.1476 | 7.54 | 40.1201 | 40.1201 | 35 | 0.016 | 3 | 25.6258 | 0.016 | 1.5 | NA | NA | 25.6258 | 0.016 | 26.1964 | 0.023376 | 0.94431 | 0.68306
89 | T2 | 1 | 0.0025 | 1 | 1 | 0.65 | 919.4885 | 7.54 | 40.0724 | 40.0724 | 35 | 0.016 | 3 | 24.7496 | 0.016 | 1.95 | NA | NA | 24.7496 | 0.016 | 26.1474 | 0.021832 | 1.0347 | 0.74691
90 | T2 | 1 | 0.0025 | 1 | 1 | 0.8 | 921.743 | 7.54 | 40.0267 | 40.0267 | 35 | 0.016 | 3 | 23.9092 | 0.016 | 2.4 | NA | NA | 23.9092 | 0.016 | 25.3753 | 0.021033 | 1.1151 | 0.80814
91 | T3 | 1 | 0.0025 | 1 | 1 | 0.2 | 913.3464 | 7.54 | 40.1978 | 40.1978 | 35 | 0.016 | 3 | 35 | 0.016 | 0.6 | NA | NA | 27.0563 | 0.016 | 40.4841 | 0.029751 | 0.79362 | 0.57883
92 | T3 | 1 | 0.0025 | 1 | 1 | 0.35 | 916.8617 | 7.54 | 40.1259 | 40.1259 | 35 | 0.016 | 3 | 35 | 0.016 | 1.05 | NA | NA | 25.7331 | 0.016 | 37.4479 | 0.025672 | 0.93426 | 0.67524
93 | T3 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.4815 | 7.54 | 40.1133 | 40.1133 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.5006 | 0.016 | 35.195 | 0.023581 | 0.95436 | 0.69218
94 | T3 | 1 | 0.0025 | 1 | 1 | 0.65 | 916.7664 | 7.54 | 40.1278 | 40.1278 | 35 | 0.016 | 3 | 35 | 0.016 | 1.95 | NA | NA | 25.7689 | 0.016 | 34.1081 | 0.02209 | 0.92422 | 0.67264
95 | T3 | 1 | 0.0025 | 1 | 1 | 0.8 | 914.9113 | 7.54 | 40.1657 | 40.1657 | 35 | 0.016 | 3 | 35 | 0.016 | 2.4 | NA | NA | 26.4662 | 0.016 | 33.9009 | 0.020748 | 0.8539 | 0.62182
96 | T4 | 1 | 0.0025 | 1 | 1 | 0.2 | 908.6307 | 7.54 | 40.2948 | 40.2948 | 35 | 0.016 | 3 | 35 | 0.016 | 0.6 | NA | NA | 28.8444 | 0.016 | 34.5577 | 0.028593 | 0.62284 | 0.44853
97 | T4 | 1 | 0.0025 | 1 | 1 | 0.35 | 914.3418 | 7.54 | 40.1774 | 40.1774 | 35 | 0.016 | 3 | 35 | 0.016 | 1.05 | NA | NA | 26.6808 | 0.016 | 35.7159 | 0.025291 | 0.83381 | 0.60619
98 | T4 | 1 | 0.0025 | 1 | 1 | 0.5 | 917.1476 | 7.54 | 40.1201 | 40.1201 | 35 | 0.016 | 3 | 35 | 0.016 | 1.5 | NA | NA | 25.6258 | 0.016 | 35.1924 | 0.023481 | 0.94431 | 0.68306
99 | T4 | 1 | 0.0025 | 1 | 1 | 0.65 | 917.911 | 7.54 | 40.1045 | 40.1045 | 35 | 0.016 | 3 | 35 | 0.016 | 1.95 | NA | NA | 25.3397 | 0.016 | 34.7123 | 0.02211 | 0.97445 | 0.70391
100 | T4 | 1 | 0.0025 | 1 | 1 | 0.8 | 917.3861 | 7.54 | 40.1152 | 40.1152 | 35 | 0.016 | 3 | 35 | 0.016 | 2.4 | NA | NA | 25.5364 | 0.016 | 34.4682 | 0.020986 | 0.95436 | 0.68958