## Liu2019
Paper information
Authors | Liu et al.
Title | Experimental and numerical investigation of a high-eﬃciency dew-point evaporative cooler
Year | 2019
Data type | Experimental data, extracted from table
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Sprayed-water theory |  | counterflow |  | counterflow |  | parallel
Water recirculation | Yes
Wall material | Aluminium
Configuration | PCC
Geometry |  |  |  | Measurement uncertainties
Length | 1.05 | m |  | Temperature | 0.1 | K
Width | 0.716 | m |  | Humidity | 3.2441 | %
Height | 1.0062 | m |  | Air flow | 6.3 | %
Channel height | 0.0043 | m
Wall thickness | NA | m
Number of channels | 234 | -
Operating conditions
Primary fluid velocity | 1.6-2.5 | m/s
Secondary fluid velocity | 0.75-1 | m/s
Secondary-to-Primary flow rate ratio | 0.36-0.54 | kg/kg
Water supplied | 0.1 - 0.266 | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.403 | 1165.1947 | 8.23 | 28.0598 | 28.0598 | 38.3 | 0.010742 | 2.4314 | 23.4 | 0.010742 | 0.97985 | 26 | 0.0022792 | 23.4 | 0.010742 | NA | NA | 0.955 | 0.648
2 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.437 | 1084.2732 | 8.23 | 28.0375 | 28.0375 | 38.1 | 0.010454 | 2.2579 | 23 | 0.010454 | 0.98669 | 26 | 0.0022792 | 23 | 0.010454 | NA | NA | 0.962 | 0.651
3 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.437 | 1085.8546 | 8.23 | 28.0184 | 28.0184 | 38.1 | 0.010454 | 2.2579 | 22.5 | 0.010454 | 0.98669 | 26 | 0.0008547 | 22.5 | 0.010454 | NA | NA | 0.969 | 0.647
4 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.445 | 1104.1162 | 8.23 | 28.0043 | 28.0043 | 38.1 | 0.0099019 | 2.2918 | 22.1 | 0.0099019 | 1.0199 | 26 | 0.00091168 | 22.1 | 0.0099019 | NA | NA | 0.994 | 0.664
5 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.463 | 1054.1075 | 8.23 | 28.0255 | 28.0255 | 38.4 | 0.0090752 | 2.1893 | 22.3 | 0.0090752 | 1.0136 | 25.2 | 0.0020513 | 22.3 | 0.0090752 | NA | NA | 0.955 | 0.626
6 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.453 | 1037.42 | 8.23 | 28.0034 | 28.0034 | 38.4 | 0.0086882 | 2.1499 | 21.7 | 0.0086882 | 0.97392 | 25.2 | 0.0018234 | 21.7 | 0.0086882 | NA | NA | 0.977 | 0.635
7 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.455 | 1043.7654 | 8.23 | 27.9827 | 27.9827 | 38.8 | 0.0076524 | 2.1569 | 20.7 | 0.0076524 | 0.98137 | 24.4 | 0.0018234 | 20.7 | 0.0076524 | NA | NA | 0.996 | 0.633
8 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.437 | 1016.5697 | 8.23 | 27.9644 | 27.9644 | 38.6 | 0.0072666 | 2.0967 | 20.4 | 0.0072666 | 0.91626 | 24 | 0.0018234 | 20.4 | 0.0072666 | NA | NA | 0.963 | 0.593
9 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.381 | 1211.3178 | 8.23 | 27.9624 | 27.9624 | 37.6 | 0.0064299 | 2.4954 | 21.3 | 0.0064299 | 0.95074 | 24.5 | 0.0018234 | 21.3 | 0.0064299 | NA | NA | 0.892 | 0.544
10 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.536 | 913.4475 | 8.23 | 27.9275 | 27.9275 | 37.8 | 0.0065008 | 1.8769 | 20.2 | 0.0065008 | 1.006 | 23.9 | 0.0022792 | 20.2 | 0.0065008 | NA | NA | 0.959 | 0.587
11 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.461 | 830.3993 | 8.23 | 27.3316 | 27.3316 | 25.4 | 0.0058577 | 1.6286 | 17.2 | 0.0058577 | 0.7508 | 20 | 0.0022792 | 17.2 | 0.0058577 | NA | NA | 0.749 | 0.429
12 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.361 | 1169.9055 | 8.23 | 28.0973 | 28.0973 | 38.4 | 0.012536 | 2.4538 | 24.4 | 0.012536 | 0.8858 | 25 | 0.0022792 | 24.4 | 0.012536 | NA | NA | 0.966 | 0.714
13 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.462 | 1011.5655 | 8.23 | 28.0372 | 28.0372 | 38.6 | 0.01057 | 2.1067 | 22.5 | 0.01057 | 0.97331 | 25 | 0.0022792 | 22.5 | 0.01057 | NA | NA | 1.006 | 0.682
14 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.447 | 966.41 | 8.23 | 28.0368 | 28.0368 | 37.3 | 0.01393 | 2.0211 | 24 | 0.01393 | 0.90345 | 25 | 0.0022792 | 24 | 0.01393 | NA | NA | 1.039 | 0.739
15 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.395 | 1070.8177 | 8.23 | 28.0737 | 28.0737 | 38.3 | 0.014376 | 2.2471 | 24 | 0.014376 | 0.8876 | 25 | 0.0022792 | 24 | 0.014376 | NA | NA | 1.075 | 0.773
16 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.402 | 1167.5735 | 8.23 | 28.1412 | 28.1412 | 38.7 | 0.014697 | 2.4638 | 25.4 | 0.014697 | 0.99044 | 27 | 0.0022792 | 25.4 | 0.014697 | NA | NA | 0.993 | 0.715
17 | A | 1.05 | 0.0043 | 0.716 | 1.1 | 0.391 | 1206.9405 | 8.23 | 28.0912 | 28.0912 | 37.6 | 0.013453 | 2.5332 | 25.1 | 0.013453 | 0.99047 | 27 | 0.0022792 | 25.1 | 0.013453 | NA | NA | 0.993 | 0.711

## Pakari2019
Paper information
Authors | Pakari & Ghani
Title | Regression models for performance prediction of counter ﬂow dew point evaporative cooling systems
Year | 2019
Data type | Experimental data (extracted from graphs) and numerical data (from table)
Description | Numerically testing of 90 combinations of geometrical parameters and operating conditions to evaluate the performance of D-IEC. Validation of the model performed with a vertical 100-channel D-IEC with dry channels made of corrugated plastic sheets stacked next to each other, and wicking paper pasted on the wet channels to enhance their wettability. Cooling system tested by varying the primary air extraction ratio and the inlet air conditions (temperature, relative humidity, and velocity).
HEX characteristics |  |  | Configuration
HEX type | D-IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Wet surface theory |  | counterflow |  | counterflow |  | parallel
Water recirculation | Yes
Wall material | Plastic sheets
Configuration | PCC
Geometry |  |  |  | Measurement uncertainties
Length | 0.5 | m |  | Temperature | 0.2 | K
Width | 0.3 | m |  | Humidity | 4.6512 | %
Height | 0.22 | m |  | Air flow | 5.8824 | %
Channel height | 0.002 | m
Wall thickness | 0.0002 | m
Number of channels | 100 | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 0.5-1.5 | m/s |  | E | Experimental
Secondary fluid velocity | 0.15-0.52 | m/s |  | N | Numerical
Secondary-to-Primary flow rate ratio | 0.15-0.5 | kg/kg
Water supplied | NA | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | E | 0.5 | 0.002 | 0.3 | 1 | 0.332 | 2.81 | 2.81 | 18.3515 | 49.2422 | 29.2 | 0.01094 | 0.59 | 17.9096 | 0.01094 | 0.19588 | NA | NA | 17.9096 | 0.01094 | NA | NA | 1.2305 | 0.81509
2 | E | 0.5 | 0.002 | 0.3 | 1 | 0.447 | 2.81 | 2.81 | 18.337 | 49.2033 | 30.1 | 0.0080015 | 0.55 | 16.3321 | 0.0080015 | 0.24585 | NA | NA | 16.3321 | 0.0080015 | NA | NA | 1.1409 | 0.70748
3 | E | 0.5 | 0.002 | 0.3 | 1 | 0.236 | 2.81 | 2.81 | 18.4096 | 49.3979 | 30.2 | 0.00832 | 0.82 | 19.0528 | 0.00832 | 0.19352 | NA | NA | 19.0528 | 0.00832 | NA | NA | 0.93847 | 0.58727
4 | E | 0.5 | 0.002 | 0.3 | 1 | 0.38 | 2.81 | 2.81 | 18.3681 | 49.2867 | 30.3 | 0.008095 | 0.62 | 17.3381 | 0.008095 | 0.2356 | NA | NA | 17.3381 | 0.008095 | NA | NA | 1.069 | 0.66511
5 | E | 0.5 | 0.002 | 0.3 | 1 | 0.37 | 2.81 | 2.81 | 18.4414 | 49.4833 | 30.3 | 0.0091903 | 0.87 | 20.2265 | 0.0091903 | 0.3219 | NA | NA | 20.2265 | 0.0091903 | NA | NA | 0.89468 | 0.57254
6 | E | 0.5 | 0.002 | 0.3 | 1 | 0.172 | 2.81 | 2.81 | 18.5788 | 49.852 | 30.5 | 0.0092978 | 0.95 | 25.3783 | 0.0092978 | 0.1634 | NA | NA | 25.3783 | 0.0092978 | NA | NA | 0.45276 | 0.29068
7 | E | 0.5 | 0.002 | 0.3 | 1 | 0.359 | 2.81 | 2.81 | 18.6002 | 49.9094 | 32.4 | 0.017593 | 0.57 | 24.7763 | 0.017593 | 0.20463 | NA | NA | 24.7763 | 0.017593 | NA | NA | 1.0801 | 0.79338
8 | E | 0.5 | 0.002 | 0.3 | 1 | 0.367 | 2.81 | 2.81 | 18.555 | 49.7881 | 35.1 | 0.0099283 | 0.54 | 19.8835 | 0.0099283 | 0.19818 | NA | NA | 19.8835 | 0.0099283 | NA | NA | 1.0849 | 0.71677
9 | E | 0.5 | 0.002 | 0.3 | 1 | 0.322 | 2.81 | 2.81 | 18.6785 | 50.1196 | 36.8 | 0.011712 | 0.58 | 23.1149 | 0.011712 | 0.18676 | NA | NA | 23.1149 | 0.011712 | NA | NA | 0.97745 | 0.67068
10 | E | 0.5 | 0.002 | 0.3 | 1 | 0.369 | 2.81 | 2.81 | 18.5893 | 49.8803 | 38.2 | 0.0092317 | 0.51 | 18.0849 | 0.0092317 | 0.18819 | NA | NA | 18.0849 | 0.0092317 | NA | NA | 1.2039 | 0.79109
11 | E | 0.5 | 0.002 | 0.3 | 1 | 0.376 | 2.81 | 2.81 | 18.7936 | 50.4283 | 40.2 | 0.015088 | 0.83 | 24.4638 | 0.015088 | 0.31208 | NA | NA | 24.4638 | 0.015088 | NA | NA | 1.0933 | 0.79262
12 | E | 0.5 | 0.002 | 0.3 | 1 | 0.483 | 2.81 | 2.81 | 18.7685 | 50.361 | 42.2 | 0.0093493 | 0.67 | 21.0876 | 0.0093493 | 0.32361 | NA | NA | 21.0876 | 0.0093493 | NA | NA | 1.0835 | 0.72212
13 | E | 0.5 | 0.002 | 0.3 | 1 | 0.308 | 2.81 | 2.81 | 18.8875 | 50.6805 | 43.9 | 0.011389 | 0.59 | 24.2047 | 0.011389 | 0.18172 | NA | NA | 24.2047 | 0.011389 | NA | NA | 1.0152 | 0.70502
14 | E | 0.5 | 0.002 | 0.3 | 1 | 0.417 | 2.81 | 2.81 | 18.8673 | 50.6263 | 44.1 | 0.014454 | 0.77 | 23.4349 | 0.014454 | 0.32109 | NA | NA | 23.4349 | 0.014454 | NA | NA | 1.1669 | 0.84587
15 | E | 0.5 | 0.002 | 0.3 | 1 | 0.337 | 2.81 | 2.81 | 18.8137 | 50.4823 | 44.2 | 0.0098076 | 0.55 | 20.8895 | 0.0098076 | 0.18535 | NA | NA | 20.8895 | 0.0098076 | NA | NA | 1.1298 | 0.76392
16 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
17 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7195 | 36.8131 | 40.25 | 0.019028 | 0.75 | 27.5 | 0.019028 | 0.17812 | NA | NA | 27.5 | 0.019028 | NA | NA | 1.05 | 0.78717
18 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7414 | 36.8718 | 40.25 | 0.019028 | 0.75 | 28.7 | 0.019028 | 0.17812 | NA | NA | 28.7 | 0.019028 | NA | NA | 0.94 | 0.71309
19 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
20 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4004 | 35.957 | 30.75 | 0.0055148 | 1.25 | 19 | 0.0055148 | 0.51562 | NA | NA | 19 | 0.0055148 | NA | NA | 0.81 | 0.4605
21 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.727 | 36.8334 | 40.25 | 0.0093704 | 1.25 | 27.2 | 0.0093704 | 0.29688 | NA | NA | 27.2 | 0.0093704 | NA | NA | 0.72 | 0.47886
22 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
23 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.7122 | 36.7935 | 40.25 | 0.019028 | 0.75 | 27.1 | 0.019028 | 0.30937 | NA | NA | 27.1 | 0.019028 | NA | NA | 1.07 | 0.81187
24 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8474 | 23.74 | 40.25 | 0.0093704 | 0.75 | 24.3 | 0.0093704 | 0.30937 | NA | NA | 24.3 | 0.0093704 | NA | NA | 0.88 | 0.58527
25 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.928 | 23.9563 | 40.25 | 0.019028 | 1.25 | 31.8 | 0.019028 | 0.51562 | NA | NA | 31.8 | 0.019028 | NA | NA | 0.69 | 0.52169
26 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7258 | 23.4136 | 30.75 | 0.011128 | 1.25 | 23.8 | 0.011128 | 0.29688 | NA | NA | 23.8 | 0.011128 | NA | NA | 0.69 | 0.45902
27 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6757 | 23.2794 | 30.75 | 0.0055148 | 1.25 | 19.4 | 0.0055148 | 0.51562 | NA | NA | 19.4 | 0.0055148 | NA | NA | 0.78 | 0.44482
28 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.6733 | 23.2729 | 30.75 | 0.0055148 | 0.75 | 19.2 | 0.0055148 | 0.17812 | NA | NA | 19.2 | 0.0055148 | NA | NA | 0.79 | 0.45266
29 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
30 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4294 | 36.0347 | 30.75 | 0.011128 | 1.25 | 20.8 | 0.011128 | 0.51562 | NA | NA | 20.8 | 0.011128 | NA | NA | 0.99 | 0.65715
31 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7113 | 23.3748 | 30.75 | 0.011128 | 1.25 | 22.6 | 0.011128 | 0.51562 | NA | NA | 22.6 | 0.011128 | NA | NA | 0.81 | 0.53827
32 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.9374 | 23.9816 | 40.25 | 0.019028 | 1.25 | 32.6 | 0.019028 | 0.29688 | NA | NA | 32.6 | 0.019028 | NA | NA | 0.63 | 0.4723
33 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
34 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.6379 | 36.5943 | 40.25 | 0.0093704 | 0.75 | 22.4 | 0.0093704 | 0.17812 | NA | NA | 22.4 | 0.0093704 | NA | NA | 0.99 | 0.65499
35 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7541 | 36.9061 | 40.25 | 0.019028 | 1.25 | 29.4 | 0.019028 | 0.29688 | NA | NA | 29.4 | 0.019028 | NA | NA | 0.89 | 0.66987
36 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.4314 | 27.9902 | 26 | 0.0062836 | 1 | 17.2 | 0.0062836 | 0.325 | NA | NA | 17.2 | 0.0062836 | NA | NA | 0.81 | 0.46574
37 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
38 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.6989 | 23.3415 | 30.75 | 0.0055148 | 1.25 | 21.3 | 0.0055148 | 0.29688 | NA | NA | 21.3 | 0.0055148 | NA | NA | 0.65 | 0.37036
39 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.6916 | 23.3219 | 30.75 | 0.0055148 | 0.75 | 20.7 | 0.0055148 | 0.17812 | NA | NA | 20.7 | 0.0055148 | NA | NA | 0.69 | 0.39388
40 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.875 | 23.8141 | 40.25 | 0.0093704 | 0.75 | 26.6 | 0.0093704 | 0.17812 | NA | NA | 26.6 | 0.0093704 | NA | NA | 0.76 | 0.50087
41 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.6881 | 36.7289 | 40.25 | 0.0093704 | 1.25 | 25.1 | 0.0093704 | 0.29688 | NA | NA | 25.1 | 0.0093704 | NA | NA | 0.84 | 0.55591
42 | N | 1 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6418 | 28.5549 | 35.5 | 0.010892 | 1 | 22.2 | 0.010892 | 0.325 | NA | NA | 22.2 | 0.010892 | NA | NA | 0.98 | 0.65777
43 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.3759 | 35.8913 | 30.75 | 0.0055148 | 0.75 | 17.7 | 0.0055148 | 0.17812 | NA | NA | 17.7 | 0.0055148 | NA | NA | 0.9 | 0.51145
44 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.9115 | 23.912 | 40.25 | 0.019028 | 0.75 | 30.4 | 0.019028 | 0.17812 | NA | NA | 30.4 | 0.019028 | NA | NA | 0.81 | 0.60813
45 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.2985 | 35.6836 | 30.75 | 0.0055148 | 0.75 | 13.6 | 0.0055148 | 0.30937 | NA | NA | 13.6 | 0.0055148 | NA | NA | 1.17 | 0.67214
46 | N | 0.5 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6958 | 28.6999 | 35.5 | 0.010892 | 1 | 25.9 | 0.010892 | 0.325 | NA | NA | 25.9 | 0.010892 | NA | NA | 0.7 | 0.47478
47 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
48 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7294 | 23.4233 | 30.75 | 0.011128 | 1.25 | 24.1 | 0.011128 | 0.51562 | NA | NA | 24.1 | 0.011128 | NA | NA | 0.66 | 0.4392
49 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.5 | 2.81 | 2.81 | 10.6462 | 28.5667 | 35.5 | 0.010892 | 1 | 22.5 | 0.010892 | 0.5 | NA | NA | 22.5 | 0.010892 | NA | NA | 0.96 | 0.64293
50 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.6714 | 36.684 | 40.25 | 0.0093704 | 0.75 | 24.2 | 0.0093704 | 0.17812 | NA | NA | 24.2 | 0.0093704 | NA | NA | 0.89 | 0.58894
51 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.435 | 36.0497 | 30.75 | 0.011128 | 0.75 | 21.1 | 0.011128 | 0.17812 | NA | NA | 21.1 | 0.011128 | NA | NA | 0.96 | 0.63734
52 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.3382 | 35.79 | 30.75 | 0.0055148 | 0.75 | 15.7 | 0.0055148 | 0.30937 | NA | NA | 15.7 | 0.0055148 | NA | NA | 1.03 | 0.58983
53 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6355 | 23.1714 | 30.75 | 0.0055148 | 0.75 | 16.1 | 0.0055148 | 0.30937 | NA | NA | 16.1 | 0.0055148 | NA | NA | 1 | 0.57416
54 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8161 | 23.6561 | 40.25 | 0.0093704 | 0.75 | 21.7 | 0.0093704 | 0.30937 | NA | NA | 21.7 | 0.0093704 | NA | NA | 1.03 | 0.68067
55 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
56 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6958 | 28.6999 | 35.5 | 0.010892 | 1.5 | 25.9 | 0.010892 | 0.4875 | NA | NA | 25.9 | 0.010892 | NA | NA | 0.7 | 0.47478
57 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4117 | 35.9874 | 30.75 | 0.0055148 | 1.25 | 19.6 | 0.0055148 | 0.29688 | NA | NA | 19.6 | 0.0055148 | NA | NA | 0.77 | 0.43699
58 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8761 | 23.8171 | 40.25 | 0.019028 | 0.75 | 27.4 | 0.019028 | 0.30937 | NA | NA | 27.4 | 0.019028 | NA | NA | 1.05 | 0.79335
59 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8954 | 23.8688 | 40.25 | 0.0093704 | 1.25 | 28.3 | 0.0093704 | 0.51562 | NA | NA | 28.3 | 0.0093704 | NA | NA | 0.66 | 0.43849
60 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.8885 | 29.2169 | 45 | 0.018279 | 1 | 30.3 | 0.018279 | 0.325 | NA | NA | 30.3 | 0.018279 | NA | NA | 0.9 | 0.68074
61 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.3571 | 35.8407 | 30.75 | 0.0055148 | 1.25 | 16.7 | 0.0055148 | 0.51562 | NA | NA | 16.7 | 0.0055148 | NA | NA | 0.96 | 0.55064
62 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4611 | 36.1197 | 30.75 | 0.011128 | 1.25 | 22.5 | 0.011128 | 0.29688 | NA | NA | 22.5 | 0.011128 | NA | NA | 0.82 | 0.54488
63 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6095 | 28.4682 | 35.5 | 0.0035887 | 1 | 19.6 | 0.0035887 | 0.325 | NA | NA | 19.6 | 0.0035887 | NA | NA | 0.83 | 0.43974
64 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6623 | 23.2434 | 30.75 | 0.0055148 | 0.75 | 18.3 | 0.0055148 | 0.30937 | NA | NA | 18.3 | 0.0055148 | NA | NA | 0.85 | 0.48794
65 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4536 | 36.0997 | 30.75 | 0.011128 | 0.75 | 22.1 | 0.011128 | 0.17812 | NA | NA | 22.1 | 0.011128 | NA | NA | 0.86 | 0.5713
66 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7017 | 23.3489 | 30.75 | 0.011128 | 0.75 | 21.8 | 0.011128 | 0.30937 | NA | NA | 21.8 | 0.011128 | NA | NA | 0.88 | 0.59111
67 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
68 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4163 | 35.9996 | 30.75 | 0.011128 | 0.75 | 20.1 | 0.011128 | 0.30937 | NA | NA | 20.1 | 0.011128 | NA | NA | 1.06 | 0.70339
69 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8962 | 23.8709 | 40.25 | 0.019028 | 0.75 | 29.1 | 0.019028 | 0.30937 | NA | NA | 29.1 | 0.019028 | NA | NA | 0.91 | 0.68839
70 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4816 | 36.1747 | 30.75 | 0.011128 | 1.25 | 23.6 | 0.011128 | 0.29688 | NA | NA | 23.6 | 0.011128 | NA | NA | 0.71 | 0.47223
71 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.7596 | 36.9207 | 40.25 | 0.019028 | 1.25 | 29.7 | 0.019028 | 0.51562 | NA | NA | 29.7 | 0.019028 | NA | NA | 0.87 | 0.65135
72 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.8642 | 23.7851 | 40.25 | 0.0093704 | 1.25 | 25.7 | 0.0093704 | 0.51562 | NA | NA | 25.7 | 0.0093704 | NA | NA | 0.81 | 0.5339
73 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.9068 | 23.8994 | 40.25 | 0.019028 | 1.25 | 30 | 0.019028 | 0.51562 | NA | NA | 30 | 0.019028 | NA | NA | 0.84 | 0.63282
74 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.895 | 23.8677 | 40.25 | 0.019028 | 0.75 | 29 | 0.019028 | 0.17812 | NA | NA | 29 | 0.019028 | NA | NA | 0.92 | 0.69456
75 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6156 | 36.5344 | 40.25 | 0.0093704 | 0.75 | 21.2 | 0.0093704 | 0.30937 | NA | NA | 21.2 | 0.0093704 | NA | NA | 1.05 | 0.69902
76 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
77 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7171 | 23.3905 | 30.75 | 0.0055148 | 1.25 | 22.8 | 0.0055148 | 0.29688 | NA | NA | 22.8 | 0.0055148 | NA | NA | 0.54 | 0.31157
78 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.739 | 23.4492 | 30.75 | 0.011128 | 1.25 | 24.9 | 0.011128 | 0.29688 | NA | NA | 24.9 | 0.011128 | NA | NA | 0.58 | 0.38637
79 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6155 | 28.4843 | 35.5 | 0.010892 | 0.5 | 20.4 | 0.010892 | 0.1625 | NA | NA | 20.4 | 0.010892 | NA | NA | 1.11 | 0.74679
80 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.911 | 23.9106 | 40.25 | 0.0093704 | 1.25 | 29.6 | 0.0093704 | 0.29688 | NA | NA | 29.6 | 0.0093704 | NA | NA | 0.59 | 0.39079
81 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
82 | N | 0.75 | 0.005 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 7.483 | 20.0789 | 35.5 | 0.010892 | 1 | 25.5 | 0.010892 | 0.325 | NA | NA | 25.5 | 0.010892 | NA | NA | 0.73 | 0.49456
83 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.7013 | 23.348 | 30.75 | 0.0055148 | 1.25 | 21.5 | 0.0055148 | 0.51562 | NA | NA | 21.5 | 0.0055148 | NA | NA | 0.64 | 0.36252
84 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.7268 | 36.8327 | 40.25 | 0.019028 | 1.25 | 27.9 | 0.019028 | 0.51562 | NA | NA | 27.9 | 0.019028 | NA | NA | 1.01 | 0.76248
85 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
86 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.5728 | 36.4195 | 40.25 | 0.0093704 | 0.75 | 18.9 | 0.0093704 | 0.30937 | NA | NA | 18.9 | 0.0093704 | NA | NA | 1.18 | 0.78342
87 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7065 | 23.3619 | 30.75 | 0.011128 | 0.75 | 22.2 | 0.011128 | 0.17812 | NA | NA | 22.2 | 0.011128 | NA | NA | 0.84 | 0.56469
88 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6881 | 36.7289 | 40.25 | 0.0093704 | 1.25 | 25.1 | 0.0093704 | 0.51562 | NA | NA | 25.1 | 0.0093704 | NA | NA | 0.84 | 0.55591
89 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4381 | 36.0581 | 30.75 | 0.0055148 | 1.25 | 21 | 0.0055148 | 0.29688 | NA | NA | 21 | 0.0055148 | NA | NA | 0.67 | 0.38212
90 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 8.6836 | 23.3003 | 30.75 | 0.011128 | 0.75 | 20.3 | 0.011128 | 0.30937 | NA | NA | 20.3 | 0.011128 | NA | NA | 1.03 | 0.69018
91 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
92 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.6637 | 28.6137 | 35.5 | 0.010892 | 1 | 23.7 | 0.010892 | 0.325 | NA | NA | 23.7 | 0.010892 | NA | NA | 0.86 | 0.58358
93 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.7796 | 36.9745 | 40.25 | 0.019028 | 1.25 | 30.8 | 0.019028 | 0.29688 | NA | NA | 30.8 | 0.019028 | NA | NA | 0.77 | 0.58343
94 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.8498 | 23.7464 | 40.25 | 0.0093704 | 0.75 | 24.5 | 0.0093704 | 0.17812 | NA | NA | 24.5 | 0.0093704 | NA | NA | 0.87 | 0.57793
95 | N | 0.75 | 0.002 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 18.5951 | 49.8956 | 35.5 | 0.010892 | 1 | 21.1 | 0.010892 | 0.325 | NA | NA | 21.1 | 0.010892 | NA | NA | 1.06 | 0.71217
96 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6884 | 36.7298 | 40.25 | 0.019028 | 0.75 | 25.8 | 0.019028 | 0.30937 | NA | NA | 25.8 | 0.019028 | NA | NA | 1.19 | 0.89213
97 | N | 0.625 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.7197 | 23.3975 | 30.75 | 0.011128 | 0.75 | 23.3 | 0.011128 | 0.17812 | NA | NA | 23.3 | 0.011128 | NA | NA | 0.74 | 0.49204
98 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.325 | 2.81 | 2.81 | 10.7106 | 28.7394 | 35.5 | 0.018367 | 1 | 27.4 | 0.018367 | 0.325 | NA | NA | 27.4 | 0.018367 | NA | NA | 0.9 | 0.67406
99 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.4573 | 36.1097 | 30.75 | 0.011128 | 1.25 | 22.3 | 0.011128 | 0.51562 | NA | NA | 22.3 | 0.011128 | NA | NA | 0.84 | 0.55809
100 | N | 0.625 | 0.00275 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 13.4004 | 35.957 | 30.75 | 0.0055148 | 0.75 | 19 | 0.0055148 | 0.17812 | NA | NA | 19 | 0.0055148 | NA | NA | 0.81 | 0.4605
101 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.3902 | 35.9295 | 30.75 | 0.011128 | 0.75 | 18.7 | 0.011128 | 0.30937 | NA | NA | 18.7 | 0.011128 | NA | NA | 1.19 | 0.79585
102 | N | 0.75 | 0.0035 | 0.3 | 1 | 0.15 | 2.81 | 2.81 | 10.7104 | 28.739 | 35.5 | 0.010892 | 1 | 26.9 | 0.010892 | 0.15 | NA | NA | 26.9 | 0.010892 | NA | NA | 0.63 | 0.42532
103 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.887 | 23.8463 | 40.25 | 0.0093704 | 1.25 | 27.6 | 0.0093704 | 0.29688 | NA | NA | 27.6 | 0.0093704 | NA | NA | 0.7 | 0.46418
104 | N | 0.875 | 0.00425 | 0.3 | 1 | 0.2375 | 2.81 | 2.81 | 8.9198 | 23.9342 | 40.25 | 0.019028 | 1.25 | 31.1 | 0.019028 | 0.29688 | NA | NA | 31.1 | 0.019028 | NA | NA | 0.75 | 0.56491
105 | N | 0.875 | 0.00275 | 0.3 | 1 | 0.4125 | 2.81 | 2.81 | 13.6398 | 36.5993 | 40.25 | 0.0093704 | 1.25 | 22.5 | 0.0093704 | 0.51562 | NA | NA | 22.5 | 0.0093704 | NA | NA | 0.99 | 0.65132