## DeAntonellis2017
Paper information
Authors | De Antonellis et al.
Title | Modeling and experimental study of an indirect evaporative cooler
Year | 2017
Data type | Experimental data, extracted from table and graphs
Description | Experimental study of a crossflow IEC, consisting of a commercial 118-channel plate heat exchanger with water spray nozzles installed at the inlet of the secondary channels. Investigation of the effect of the secondary air inlet conditions and sprayed water flow rate on the performance of the heat exchanger. Measurement of the air conditions at the outlet of the secondary channel, implying the possibility of performing a model validation on the secondary side as well.
HEX characteristics |  |  | Configuration
HEX type | IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Sprayed-water |  | Crossflow |  | Crossflow |  | Parallel
Water recirculation | Yes
Wall material | Aluminium alloy
Configuration | XPP
Geometry |  |  |  | Measurement uncertainties
Length | 0.47 | m |  | Temperature | 0.2 | K
Width | 0.47 | m |  | Humidity | 3.5832 | %
Height | 0.39516 | m |  | Air flow | 0.5 | %
Channel height | 0.00321 | m
Wall thickness | 0.00014 | m
Number of channels | 118 | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 1.9-3.7 | m/s |  | Test number indicates similair operating conditions
Secondary fluid velocity | 1.9-5.7 | m/s |  | NB: For T10-12 the outlet conditions on secondary side are not avaiblable
Secondary-to-Primary flow rate ratio | 1-1.54 | kg/kg
Water supplied | 0.008-0.02 | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.1553 | 7.54 | 59.3221 | 59.3221 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014446 | 23.9025 | 0.01 | 26.5057 | 0.016509 | 0.79836 | 0.52806
2 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1468.8385 | 7.54 | 59.3161 | 59.3161 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016027 | 23.9762 | 0.01 | 26.1023 | 0.016755 | 0.79116 | 0.52331
3 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.5117 | 7.54 | 59.3289 | 59.3289 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00017899 | 23.8196 | 0.01 | 25.9261 | 0.016744 | 0.80555 | 0.53282
4 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.4478 | 7.54 | 59.3655 | 59.3655 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00019913 | 23.3699 | 0.01 | 25.8864 | 0.016793 | 0.83432 | 0.55185
5 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.273 | 7.54 | 59.3433 | 59.3433 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00021978 | 23.6426 | 0.01 | 25.4489 | 0.017116 | 0.81993 | 0.54234
6 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.1274 | 7.54 | 59.3594 | 59.3594 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024048 | 23.4442 | 0.01 | 25.3295 | 0.017123 | 0.83432 | 0.55185
7 | T1 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.2234 | 7.54 | 59.3802 | 59.3802 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00026199 | 23.19 | 0.01 | 25.1364 | 0.017169 | 0.8487 | 0.56137
8 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1468.3603 | 7.54 | 59.3071 | 88.566 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00014539 | 24.0875 | 0.01 | 25.3011 | 0.015125 | 0.78397 | 0.51855
9 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1469.3036 | 7.54 | 59.3249 | 88.5927 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00016076 | 23.868 | 0.01 | 25.0852 | 0.015326 | 0.79836 | 0.52806
10 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1471.1341 | 7.54 | 59.3596 | 88.6444 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00017998 | 23.4427 | 0.01 | 24.9773 | 0.015269 | 0.83432 | 0.55185
11 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1471.2071 | 7.54 | 59.3609 | 88.6465 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00020013 | 23.4257 | 0.01 | 24.7386 | 0.015538 | 0.83432 | 0.55185
12 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1471.9119 | 7.54 | 59.3743 | 88.6664 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00022027 | 23.2622 | 0.01 | 24.8693 | 0.01561 | 0.84151 | 0.55661
13 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1472.3914 | 7.54 | 59.3833 | 88.6799 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00023998 | 23.151 | 0.01 | 24.7614 | 0.01569 | 0.8487 | 0.56137
14 | T2 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1471.8019 | 7.54 | 59.3722 | 88.6633 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00026199 | 23.2877 | 0.01 | 24.358 | 0.015769 | 0.84151 | 0.55661
15 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.6952 | 7.54 | 59.2186 | 59.2186 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00014491 | 25.1765 | 0.01 | 26.9943 | 0.01855 | 0.70486 | 0.46622
16 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1464.0215 | 7.54 | 59.2248 | 59.2248 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00016171 | 25.1001 | 0.01 | 26.6591 | 0.018513 | 0.71205 | 0.47098
17 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1464.7209 | 7.54 | 59.2381 | 59.2381 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00018142 | 24.9366 | 0.01 | 26.6307 | 0.018672 | 0.72643 | 0.48049
18 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1465.884 | 7.54 | 59.2602 | 59.2602 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00020156 | 24.6649 | 0.01 | 26.5966 | 0.018835 | 0.74082 | 0.49001
19 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1465.9117 | 7.54 | 59.2607 | 59.2607 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00022171 | 24.6584 | 0.01 | 26.3693 | 0.018892 | 0.74082 | 0.49001
20 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1466.1038 | 7.54 | 59.2643 | 59.2643 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00024192 | 24.6135 | 0.01 | 26.1477 | 0.019002 | 0.74801 | 0.49476
21 | T3 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.6429 | 7.54 | 59.2935 | 59.2935 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00026448 | 24.2546 | 0.01 | 26.2045 | 0.019135 | 0.76959 | 0.50903
22 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1465.3223 | 7.54 | 59.2495 | 88.4801 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.0001449 | 24.796 | 0.01 | 26.4545 | 0.017428 | 0.73363 | 0.48525
23 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1465.709 | 7.54 | 59.2568 | 88.491 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.0001617 | 24.7057 | 0.01 | 26.2216 | 0.017496 | 0.74082 | 0.49001
24 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1466.5144 | 7.54 | 59.2721 | 88.5138 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.00018092 | 24.5177 | 0.01 | 25.892 | 0.017466 | 0.7552 | 0.49952
25 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1467.2605 | 7.54 | 59.2862 | 88.5349 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.00020113 | 24.3437 | 0.01 | 25.9489 | 0.017758 | 0.76959 | 0.50903
26 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1468.5019 | 7.54 | 59.3097 | 88.57 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.00022127 | 24.0546 | 0.01 | 25.8239 | 0.017781 | 0.78397 | 0.51855
27 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1468.9496 | 7.54 | 59.3182 | 88.5827 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.00024142 | 23.9504 | 0.01 | 25.4773 | 0.017925 | 0.79116 | 0.52331
28 | T4 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1468.7671 | 7.54 | 59.3148 | 88.5775 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 5.7 | NA | 0.00026398 | 23.9928 | 0.01 | 25.5227 | 0.017917 | 0.79116 | 0.52331
29 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1459.5586 | 7.54 | 59.1401 | 59.1401 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00014448 | 26.1468 | 0.01 | 27.658 | 0.017734 | 0.64012 | 0.4234
30 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1460.0319 | 7.54 | 59.1491 | 59.1491 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00016228 | 26.0356 | 0.01 | 27.5614 | 0.017946 | 0.64732 | 0.42816
31 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.0106 | 7.54 | 59.1677 | 59.1677 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00018192 | 25.8057 | 0.01 | 27.442 | 0.017882 | 0.6617 | 0.43767
32 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.1868 | 7.54 | 59.171 | 59.171 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00020207 | 25.7644 | 0.01 | 27.3227 | 0.018102 | 0.6617 | 0.43767
33 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.0062 | 7.54 | 59.1676 | 59.1676 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00022172 | 25.8067 | 0.01 | 26.9875 | 0.018106 | 0.6617 | 0.43767
34 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1462.0753 | 7.54 | 59.1879 | 59.1879 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00024193 | 25.556 | 0.01 | 26.7261 | 0.018341 | 0.67609 | 0.44719
35 | T5 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1462.4004 | 7.54 | 59.1941 | 59.1941 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.000264 | 25.4797 | 0.01 | 26.2886 | 0.018432 | 0.68328 | 0.45195
36 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1456.905 | 7.54 | 59.0897 | 88.2414 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00014492 | 26.7716 | 0.01 | 27.8966 | 0.016228 | 0.58978 | 0.3901
37 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1458.192 | 7.54 | 59.1141 | 88.2779 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00016079 | 26.4684 | 0.01 | 27.6523 | 0.016407 | 0.61135 | 0.40437
38 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1458.2343 | 7.54 | 59.1149 | 88.2791 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00018094 | 26.4584 | 0.01 | 27.0955 | 0.016524 | 0.61135 | 0.40437
39 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1459.1516 | 7.54 | 59.1324 | 88.3052 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00020208 | 26.2425 | 0.01 | 26.9761 | 0.016721 | 0.63293 | 0.41865
40 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1460.3373 | 7.54 | 59.1549 | 88.3388 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00022172 | 25.9638 | 0.01 | 26.8398 | 0.016592 | 0.64732 | 0.42816
41 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1461.8222 | 7.54 | 59.1831 | 88.3809 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00024243 | 25.6153 | 0.01 | 26.7091 | 0.01679 | 0.67609 | 0.44719
42 | T6 | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1462.2515 | 7.54 | 59.1913 | 88.3931 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 5.7 | NA | 0.00026443 | 25.5147 | 0.01 | 26.5386 | 0.016964 | 0.68328 | 0.45195
43 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1457.9736 | 7.54 | 59.11 | 59.11 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.00014357 | 26.5198 | 0.01 | NA | NA | 0.61135 | 0.40437
44 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1458.4779 | 7.54 | 59.1196 | 59.1196 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.00015929 | 26.4011 | 0.01 | NA | NA | 0.61855 | 0.40913
45 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1459.2853 | 7.54 | 59.1349 | 59.1349 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.00017807 | 26.2111 | 0.01 | NA | NA | 0.63293 | 0.41865
46 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1460.2282 | 7.54 | 59.1528 | 59.1528 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.00019642 | 25.9894 | 0.01 | NA | NA | 0.64732 | 0.42816
47 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.4757 | 7.54 | 59.1765 | 59.1765 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.00021471 | 25.6966 | 0.01 | NA | NA | 0.66889 | 0.44243
48 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.9144 | 7.54 | 59.1849 | 59.1849 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.0002322 | 25.5937 | 0.01 | NA | NA | 0.67609 | 0.44719
49 | T10 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1462.3872 | 7.54 | 59.1938 | 59.1938 | 35 | 0.01 | 3.7 | 40 | 0.01 | 3.7 | NA | 0.00025226 | 25.4828 | 0.01 | NA | NA | 0.68328 | 0.45195
50 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1496.4635 | 7.54 | 59.8364 | 59.8364 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00014399 | 22.6438 | 0.01 | NA | NA | 0.7093 | 0.46192
51 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1497.235 | 7.54 | 59.8509 | 59.8509 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00015929 | 22.4697 | 0.01 | NA | NA | 0.71888 | 0.46816
52 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1497.5157 | 7.54 | 59.8561 | 59.8561 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00017807 | 22.4063 | 0.01 | NA | NA | 0.72847 | 0.4744
53 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1497.7614 | 7.54 | 59.8607 | 59.8607 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00019727 | 22.3509 | 0.01 | NA | NA | 0.72847 | 0.4744
54 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1498.0774 | 7.54 | 59.8667 | 59.8667 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00021562 | 22.2797 | 0.01 | NA | NA | 0.73806 | 0.48064
55 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1498.3935 | 7.54 | 59.8726 | 59.8726 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00023397 | 22.2084 | 0.01 | NA | NA | 0.74764 | 0.48689
56 | T11 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1498.534 | 7.54 | 59.8752 | 59.8752 | 30 | 0.01 | 3.7 | 30 | 0.01 | 3.7 | NA | 0.00025366 | 22.1768 | 0.01 | NA | NA | 0.74764 | 0.48689
57 | T12 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 756.1352 | 7.54 | 31.994 | 31.994 | 35 | 0.01 | 1.9 | 30 | 0.01 | 1.9 | NA | 0.00014229 | 23.1319 | 0.01 | NA | NA | 0.8559 | 0.56612
58 | T12 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 756.8372 | 7.54 | 32.0079 | 32.0079 | 35 | 0.01 | 1.9 | 30 | 0.01 | 1.9 | NA | 0.00019295 | 22.8153 | 0.01 | NA | NA | 0.87747 | 0.58039
59 | T12 | 0.47 | 0.00321 | 0.47 | 1 | 1 | 757.9626 | 7.54 | 32.0302 | 32.0302 | 35 | 0.01 | 1.9 | 30 | 0.01 | 1.9 | NA | 0.00027061 | 22.3087 | 0.01 | NA | NA | 0.91344 | 0.60418