## DeAntonellis2019
Paper information
Authors | De Antonellis et al.
Title | Performance measurement of a cross-flow indirect evaporative cooler: Effect of water nozzles and airflows arrangement
Year | 2019
Data type | Experimental data, extracted from graphs
Description | Experimental study of a crossflow IEC, consisting of a commercial 118-channel plate heat exchanger with water spray nozzles installed at the inlet of the secondary channels. Investigation of the effect of water nozzles and airflow arrangement by testing 6 different orientations of the IEC (cfr. Figure).
HEX characteristics |  |  | Configuration
HEX type | IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Sprayed-water |  | crossflow |  | crossflow |  | parallel
Water recirculation | No
Wall material | Aluminium alloy
Configuration | XPP
Geometry |  |  |  | Measurement uncertainties
Length | 0.47 | m |  | Temperature | 0.2 | K
Width | 0.47 | m |  | Humidity | 1 | %
Height | 0.39879 | m |  | Air flow | 0.5 | %
Channel height | 0.00321 | m
Wall thickness | 0.00014 | m
Number of channels | 119 | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 3.7 | m/s |  | Indicates the orientation of the heat exchanger
Secondary fluid velocity | 3.7-5.7 | m/s
Secondary-to-Primary flow rate ratio | 1-1.54 | kg/kg
Water supplied | 0.008-0.018 | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_swo | epsilon_wb | epsilon_dp
1 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1466.5784 | 7.54 | 31.214 | 31.214 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014455 | 24.5028 | 0.01 | NA | NA | 0.75521 | 0.49939
2 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.6518 | 7.54 | 31.2033 | 31.2033 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016269 | 24.2526 | 0.01 | NA | NA | 0.77266 | 0.51129
3 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.1447 | 7.54 | 31.1884 | 31.1884 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020619 | 23.905 | 0.01 | NA | NA | 0.79766 | 0.52783
4 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.7 | 7.54 | 31.173 | 31.173 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0002525 | 23.5435 | 0.01 | NA | NA | 0.82448 | 0.54503
5 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.4187 | 7.54 | 31.1658 | 31.1658 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00030381 | 23.3766 | 0.01 | NA | NA | 0.83594 | 0.55296
6 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1462.2975 | 7.54 | 31.2568 | 31.2568 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014348 | 25.5039 | 0.01 | NA | NA | 0.68307 | 0.45176
7 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.544 | 7.54 | 31.2443 | 31.2443 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00015959 | 25.2119 | 0.01 | NA | NA | 0.70365 | 0.46565
8 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1465.6848 | 7.54 | 31.2229 | 31.2229 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020001 | 24.7114 | 0.01 | NA | NA | 0.73984 | 0.48946
9 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.6518 | 7.54 | 31.2033 | 31.2033 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024246 | 24.2526 | 0.01 | NA | NA | 0.77318 | 0.51129
10 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.2045 | 7.54 | 31.1878 | 31.1878 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029127 | 23.8911 | 0.01 | NA | NA | 0.7987 | 0.52849
11 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1453.4435 | 7.54 | 31.3459 | 31.3459 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014151 | 27.5894 | 0.01 | NA | NA | 0.53333 | 0.35255
12 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1455.7961 | 7.54 | 31.3222 | 31.3222 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016033 | 27.0333 | 0.01 | NA | NA | 0.57292 | 0.379
13 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1459.1591 | 7.54 | 31.2883 | 31.2883 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00019999 | 26.2408 | 0.01 | NA | NA | 0.63021 | 0.41671
14 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.4846 | 7.54 | 31.2449 | 31.2449 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024283 | 25.2258 | 0.01 | NA | NA | 0.70339 | 0.46499
15 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1466.1017 | 7.54 | 31.2188 | 31.2188 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00028884 | 24.614 | 0.01 | NA | NA | 0.74687 | 0.49409
16 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1450.6872 | 7.54 | 31.3738 | 31.3738 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014449 | 28.2429 | 0.01 | NA | NA | 0.4862 | 0.32146
17 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1452.3869 | 7.54 | 31.3566 | 31.3566 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016138 | 27.8397 | 0.01 | NA | NA | 0.51484 | 0.34064
18 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1456.2084 | 7.54 | 31.318 | 31.318 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020065 | 26.9359 | 0.01 | NA | NA | 0.58021 | 0.38363
19 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1459.0409 | 7.54 | 31.2895 | 31.2895 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0002457 | 26.2686 | 0.01 | NA | NA | 0.62786 | 0.41538
20 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.2896 | 7.54 | 31.2669 | 31.2669 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029529 | 25.7402 | 0.01 | NA | NA | 0.66589 | 0.44052
21 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.324 | 7.54 | 31.1866 | 31.1866 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0001435 | 23.8633 | 0.01 | NA | NA | 0.80078 | 0.52981
22 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1468.8459 | 7.54 | 31.1914 | 31.1914 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016144 | 23.9745 | 0.01 | NA | NA | 0.79349 | 0.52452
23 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.9993 | 7.54 | 31.17 | 31.17 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020176 | 23.474 | 0.01 | NA | NA | 0.82865 | 0.54833
24 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.0592 | 7.54 | 31.1694 | 31.1694 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024391 | 23.4601 | 0.01 | NA | NA | 0.83021 | 0.54899
25 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.7183 | 7.54 | 31.1628 | 31.1628 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029118 | 23.3071 | 0.01 | NA | NA | 0.84115 | 0.55627
26 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1469.0252 | 7.54 | 31.1896 | 31.1896 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00014491 | 23.9328 | 0.01 | NA | NA | 0.79576 | 0.5265
27 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1469.8622 | 7.54 | 31.1813 | 31.1813 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00016415 | 23.7381 | 0.01 | NA | NA | 0.81006 | 0.53577
28 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1470.8796 | 7.54 | 31.1712 | 31.1712 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00020734 | 23.5018 | 0.01 | NA | NA | 0.82694 | 0.54701
29 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1471.9581 | 7.54 | 31.1605 | 31.1605 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00025279 | 23.2515 | 0.01 | NA | NA | 0.84535 | 0.55892
30 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1472.6778 | 7.54 | 31.1533 | 31.1533 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.0003022 | 23.0847 | 0.01 | NA | NA | 0.85714 | 0.56685
31 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1463.247 | 7.54 | 31.2473 | 31.2473 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00014274 | 25.2814 | 0.01 | NA | NA | 0.69912 | 0.46235
32 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1464.4948 | 7.54 | 31.2348 | 31.2348 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00016047 | 24.9894 | 0.01 | NA | NA | 0.72031 | 0.47624
33 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1466.638 | 7.54 | 31.2134 | 31.2134 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00020177 | 24.4889 | 0.01 | NA | NA | 0.7558 | 0.50005
34 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1468.4278 | 7.54 | 31.1956 | 31.1956 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00024506 | 24.0718 | 0.01 | NA | NA | 0.78593 | 0.51989
35 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1470.8796 | 7.54 | 31.1712 | 31.1712 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00029117 | 23.5018 | 0.01 | NA | NA | 0.82729 | 0.54701
36 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1456.0317 | 7.54 | 31.3198 | 31.3198 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00014227 | 26.9776 | 0.01 | NA | NA | 0.577 | 0.38165
37 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1457.8596 | 7.54 | 31.3014 | 31.3014 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00016047 | 26.5466 | 0.01 | NA | NA | 0.60813 | 0.40215
38 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1460.5789 | 7.54 | 31.274 | 31.274 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00020102 | 25.9071 | 0.01 | NA | NA | 0.65356 | 0.43258
39 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1463.3064 | 7.54 | 31.2467 | 31.2467 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00024317 | 25.2675 | 0.01 | NA | NA | 0.70027 | 0.46301
40 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1466.2208 | 7.54 | 31.2176 | 31.2176 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00029117 | 24.5862 | 0.01 | NA | NA | 0.74877 | 0.49542
41 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1450.5115 | 7.54 | 31.3756 | 31.3756 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00014227 | 28.2846 | 0.01 | NA | NA | 0.48317 | 0.31947
42 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1452.3869 | 7.54 | 31.3566 | 31.3566 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.0001634 | 27.8397 | 0.01 | NA | NA | 0.51482 | 0.34064
43 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1455.6194 | 7.54 | 31.3239 | 31.3239 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00019998 | 27.075 | 0.01 | NA | NA | 0.57019 | 0.37702
44 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1458.2729 | 7.54 | 31.2972 | 31.2972 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00024393 | 26.4493 | 0.01 | NA | NA | 0.61486 | 0.40678
45 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1460.5789 | 7.54 | 31.274 | 31.274 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00029343 | 25.9071 | 0.01 | NA | NA | 0.65418 | 0.43258
46 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1469.3838 | 7.54 | 31.186 | 31.186 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00014303 | 23.8494 | 0.01 | NA | NA | 0.80162 | 0.53047
47 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1471.4187 | 7.54 | 31.1658 | 31.1658 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00016047 | 23.3766 | 0.01 | NA | NA | 0.83606 | 0.55296
48 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1472.1379 | 7.54 | 31.1587 | 31.1587 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00020225 | 23.2098 | 0.01 | NA | NA | 0.84835 | 0.5609
49 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1473.4581 | 7.54 | 31.1456 | 31.1456 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.0002443 | 22.9039 | 0.01 | NA | NA | 0.87032 | 0.57545
50 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1.5405 | 1473.7584 | 7.54 | 31.1426 | 31.1426 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 5.7 | NA | 0.00029164 | 22.8344 | 0.01 | NA | NA | 0.87497 | 0.57876
51 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1466.5784 | 7.54 | 31.214 | 31.214 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014438 | 24.5028 | 0.01 | NA | NA | 0.75509 | 0.49939
52 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.5921 | 7.54 | 31.2039 | 31.2039 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016265 | 24.2665 | 0.01 | NA | NA | 0.77238 | 0.51063
53 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.0849 | 7.54 | 31.189 | 31.189 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020624 | 23.9189 | 0.01 | NA | NA | 0.79724 | 0.52717
54 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.7 | 7.54 | 31.173 | 31.173 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00025215 | 23.5435 | 0.01 | NA | NA | 0.82413 | 0.54503
55 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.4187 | 7.54 | 31.1658 | 31.1658 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00030385 | 23.3766 | 0.01 | NA | NA | 0.83576 | 0.55296
56 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.5324 | 7.54 | 31.2045 | 31.2045 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00014478 | 24.2804 | 0.01 | NA | NA | 0.77122 | 0.50997
57 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1468.3681 | 7.54 | 31.1962 | 31.1962 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00016266 | 24.0857 | 0.01 | NA | NA | 0.78459 | 0.51923
58 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.5034 | 7.54 | 31.1849 | 31.1849 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00020441 | 23.8215 | 0.01 | NA | NA | 0.80422 | 0.5318
59 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.8796 | 7.54 | 31.1712 | 31.1712 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00025032 | 23.5018 | 0.01 | NA | NA | 0.82674 | 0.54701
60 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.6584 | 7.54 | 31.1634 | 31.1634 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00030154 | 23.321 | 0.01 | NA | NA | 0.84041 | 0.55561
61 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.7816 | 7.54 | 31.2419 | 31.2419 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00014404 | 25.1563 | 0.01 | NA | NA | 0.70756 | 0.4683
62 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1464.9707 | 7.54 | 31.2301 | 31.2301 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00016121 | 24.8782 | 0.01 | NA | NA | 0.72834 | 0.48153
63 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1468.1292 | 7.54 | 31.1985 | 31.1985 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00020577 | 24.1413 | 0.01 | NA | NA | 0.78052 | 0.51658
64 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.8622 | 7.54 | 31.1813 | 31.1813 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00025042 | 23.7381 | 0.01 | NA | NA | 0.81003 | 0.53577
65 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.8197 | 7.54 | 31.1718 | 31.1718 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00030133 | 23.5157 | 0.01 | NA | NA | 0.82616 | 0.54635
66 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1453.4435 | 7.54 | 31.3459 | 31.3459 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014137 | 27.5894 | 0.01 | NA | NA | 0.53273 | 0.35255
67 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1455.7372 | 7.54 | 31.3227 | 31.3227 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016034 | 27.0472 | 0.01 | NA | NA | 0.57247 | 0.37834
68 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1459.1591 | 7.54 | 31.2883 | 31.2883 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00019951 | 26.2408 | 0.01 | NA | NA | 0.6296 | 0.41671
69 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.4846 | 7.54 | 31.2449 | 31.2449 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024276 | 25.2258 | 0.01 | NA | NA | 0.70317 | 0.46499
70 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1466.1017 | 7.54 | 31.2188 | 31.2188 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00028886 | 24.614 | 0.01 | NA | NA | 0.74655 | 0.49409
71 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1455.6783 | 7.54 | 31.3233 | 31.3233 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00014188 | 27.0611 | 0.01 | NA | NA | 0.57101 | 0.37768
72 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1458.1548 | 7.54 | 31.2984 | 31.2984 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00016024 | 26.4771 | 0.01 | NA | NA | 0.6132 | 0.40546
73 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1461.8823 | 7.54 | 31.261 | 31.261 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00020247 | 25.6012 | 0.01 | NA | NA | 0.67622 | 0.44713
74 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1464.7922 | 7.54 | 31.2318 | 31.2318 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00024582 | 24.9199 | 0.01 | NA | NA | 0.72476 | 0.47954
75 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.1149 | 7.54 | 31.2087 | 31.2087 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00029111 | 24.3777 | 0.01 | NA | NA | 0.76397 | 0.50534
76 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1448.4648 | 7.54 | 31.3963 | 31.3963 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.0001385 | 28.7712 | 0.01 | NA | NA | 0.44783 | 0.29632
77 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1452.3282 | 7.54 | 31.3572 | 31.3572 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00017819 | 27.8536 | 0.01 | NA | NA | 0.51428 | 0.33998
78 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1454.325 | 7.54 | 31.337 | 31.337 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00019824 | 27.3809 | 0.01 | NA | NA | 0.54837 | 0.36247
79 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1457.5055 | 7.54 | 31.3049 | 31.3049 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00023997 | 26.6301 | 0.01 | NA | NA | 0.60157 | 0.39819
80 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1460.5789 | 7.54 | 31.274 | 31.274 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.0002876 | 25.9071 | 0.01 | NA | NA | 0.65428 | 0.43258
81 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.324 | 7.54 | 31.1866 | 31.1866 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014333 | 23.8633 | 0.01 | NA | NA | 0.80066 | 0.52981
82 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1468.8459 | 7.54 | 31.1914 | 31.1914 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0001612 | 23.9745 | 0.01 | NA | NA | 0.79324 | 0.52452
83 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.9993 | 7.54 | 31.17 | 31.17 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020165 | 23.474 | 0.01 | NA | NA | 0.82867 | 0.54833
84 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.0592 | 7.54 | 31.1694 | 31.1694 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024385 | 23.4601 | 0.01 | NA | NA | 0.83038 | 0.54899
85 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.7183 | 7.54 | 31.1628 | 31.1628 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029109 | 23.3071 | 0.01 | NA | NA | 0.84122 | 0.55627
86 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.1015 | 7.54 | 31.1789 | 31.1789 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.0001425 | 23.6825 | 0.01 | NA | NA | 0.81388 | 0.53841
87 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.5204 | 7.54 | 31.1747 | 31.1747 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00015923 | 23.5852 | 0.01 | NA | NA | 0.82054 | 0.54304
88 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.9993 | 7.54 | 31.17 | 31.17 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00020103 | 23.474 | 0.01 | NA | NA | 0.8288 | 0.54833
89 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.078 | 7.54 | 31.1593 | 31.1593 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00024087 | 23.2237 | 0.01 | NA | NA | 0.84656 | 0.56024
90 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.3179 | 7.54 | 31.1569 | 31.1569 | 35 | 0.01 | 3.7 | 30 | 0.0134 | 3.7 | NA | 0.00028811 | 23.1681 | 0.01 | NA | NA | 0.85098 | 0.56288
91 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1465.8039 | 7.54 | 31.2217 | 31.2217 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00014262 | 24.6836 | 0.01 | NA | NA | 0.74186 | 0.49079
92 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1468.0098 | 7.54 | 31.1997 | 31.1997 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00015992 | 24.1691 | 0.01 | NA | NA | 0.77904 | 0.51526
93 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.2045 | 7.54 | 31.1878 | 31.1878 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.0002011 | 23.8911 | 0.01 | NA | NA | 0.79939 | 0.52849
94 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.9993 | 7.54 | 31.17 | 31.17 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.00024218 | 23.474 | 0.01 | NA | NA | 0.82865 | 0.54833
95 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.6584 | 7.54 | 31.1634 | 31.1634 | 35 | 0.01 | 3.7 | 36.8 | 0.0106 | 3.7 | NA | 0.0002889 | 23.321 | 0.01 | NA | NA | 0.83974 | 0.55561
96 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.3071 | 7.54 | 31.157 | 31.157 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014438 | 23.1706 | 0.01 | NA | NA | 0.85079 | 0.56274
97 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1473.058 | 7.54 | 31.1496 | 31.1496 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0001626 | 22.9966 | 0.01 | NA | NA | 0.8633 | 0.57102
98 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.9592 | 7.54 | 31.1505 | 31.1505 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0002062 | 23.0195 | 0.01 | NA | NA | 0.86172 | 0.56998
99 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1475.8101 | 7.54 | 31.1223 | 31.1223 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00025209 | 22.36 | 0.01 | NA | NA | 0.90912 | 0.60133
100 | TOP | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1477.7952 | 7.54 | 31.1027 | 31.1027 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.0003038 | 21.9021 | 0.01 | NA | NA | 0.94206 | 0.62312
101 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.207 | 7.54 | 31.2477 | 31.2477 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014324 | 25.2908 | 0.01 | NA | NA | 0.69831 | 0.46189
102 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1464.1854 | 7.54 | 31.2379 | 31.2379 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00015926 | 25.0618 | 0.01 | NA | NA | 0.71478 | 0.47278
103 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1465.7137 | 7.54 | 31.2226 | 31.2226 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00019953 | 24.7046 | 0.01 | NA | NA | 0.74046 | 0.48977
104 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.8537 | 7.54 | 31.2013 | 31.2013 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024227 | 24.2055 | 0.01 | NA | NA | 0.77642 | 0.51355
105 | TOPSIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1469.4867 | 7.54 | 31.185 | 31.185 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029112 | 23.8254 | 0.01 | NA | NA | 0.80375 | 0.53163
106 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1456.0389 | 7.54 | 31.3197 | 31.3197 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014133 | 26.976 | 0.01 | NA | NA | 0.57712 | 0.38173
107 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1458.7592 | 7.54 | 31.2923 | 31.2923 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016031 | 26.3349 | 0.01 | NA | NA | 0.62322 | 0.41222
108 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1462.7769 | 7.54 | 31.252 | 31.252 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00019953 | 25.3915 | 0.01 | NA | NA | 0.69105 | 0.45708
109 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1467.7555 | 7.54 | 31.2023 | 31.2023 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024274 | 24.2284 | 0.01 | NA | NA | 0.77477 | 0.51246
110 | SIDE | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1470.0186 | 7.54 | 31.1797 | 31.1797 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00028883 | 23.7018 | 0.01 | NA | NA | 0.8126 | 0.53748
111 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1452.8433 | 7.54 | 31.352 | 31.352 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014438 | 27.7315 | 0.01 | NA | NA | 0.52274 | 0.34576
112 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1454.7593 | 7.54 | 31.3326 | 31.3326 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016117 | 27.2782 | 0.01 | NA | NA | 0.5554 | 0.36736
113 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1458.5062 | 7.54 | 31.2949 | 31.2949 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020058 | 26.3944 | 0.01 | NA | NA | 0.61898 | 0.40942
114 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1460.3758 | 7.54 | 31.2761 | 31.2761 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024561 | 25.9548 | 0.01 | NA | NA | 0.65055 | 0.4303
115 | BOTTOM | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1463.0506 | 7.54 | 31.2493 | 31.2493 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029522 | 25.3274 | 0.01 | NA | NA | 0.69572 | 0.46018
116 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.3268 | 7.54 | 31.1568 | 31.1568 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00014324 | 23.166 | 0.01 | NA | NA | 0.85115 | 0.56298
117 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1471.6949 | 7.54 | 31.1631 | 31.1631 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00016117 | 23.3125 | 0.01 | NA | NA | 0.84058 | 0.55599
118 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1473.058 | 7.54 | 31.1496 | 31.1496 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00020143 | 22.9966 | 0.01 | NA | NA | 0.8633 | 0.57102
119 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1472.9592 | 7.54 | 31.1505 | 31.1505 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00024379 | 23.0195 | 0.01 | NA | NA | 0.86172 | 0.56998
120 | HORIZONTAL | 0.47 | 0.00321 | 0.47 | 1 | 1 | 1473.3941 | 7.54 | 31.1462 | 31.1462 | 35 | 0.01 | 3.7 | 30 | 0.0106 | 3.7 | NA | 0.00029112 | 22.9187 | 0.01 | NA | NA | 0.86891 | 0.57473