## Ren2006
Paper information
Authors | Ren & Yang
Title | An analytical model for the heat and mass transfer processes in indirect evaporative cooling with parallel/counter flow configurations
Year | 2006
Data type | Numerical and analytical, raw data, under the format used in their paper
HEX characteristics |  |  | Configuration
HEX type | IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Water film |  | parallel |  | counterflow |  | counterflow
Water recirculation | Yes
Configuration | PPC
Geometry
Length | NA | m
Width | NA | m
Height | NA | m
Channel width | NA | m
Wall thickness | NA | m
Number of channels | NA | -
Operating conditions
Primary fluid velocity | NA
Secondary fluid velocity | NA
Secondary-to-Primary flow rate ratio | NA | kg/kg
Water supplied | NA | [7 empty] | Important note : For the nomenclature refer to the original paper
| Given conditions | [7 empty] | Analytical results |  |  | Numerical results
Run | T_pdi | T_swi | w_swi | C_star_w | C_star_f | r | sigma_Lef | NTU | T_pdo | T_swo | w_swo | T_pdo | T_swo | w_swo
1 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 0.8 | 3 | 30.36 | 28.36 | 0.0239 | 30.35 | 28.35 | 0.0239
2 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 0.8 | 1 | 33.46 | 28.27 | 0.0201 | 33.45 | 28.26 | 0.0201
3 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 0.5 | 2 | 32.07 | 28.66 | 0.02166 | 32.07 | 28.65 | 0.02166
4 | 36 | 30 | 0.01622 | 0 | 3 | 1 | 1.1 | 2 | 31.45 | 27.74 | 0.02281 | 31.45 | 27.74 | 0.02281
5 | 36 | 30 | 0.01622 | 0 | 3 | 2.8 | 0.8 | 2 | 29.31 | 29.66 | 0.02466 | 29.3 | 29.66 | 0.02466
6 | 36 | 30 | 0.01622 | 0 | 0.75 | 1 | 0.8 | 2 | 25.87 | 26.77 | 0.02072 | 25.85 | 26.77 | 0.02072
7 | 36 | 30 | 0.01622 | 0.5 | 3 | 1 | 0.8 | 3 | 30.46 | 28.26 | 0.02382 | 30.45 | 28.24 | 0.0238
8 | 36 | 30 | 0.01622 | 0.5 | 3 | 8 | 0.8 | 3 | 26.73 | 30.65 | 0.02744 | 26.7 | 30.63 | 0.0274
9 | 36 | 30 | 0.01622 | 1 | 3 | 1 | 1 | 5 | 28.78 | 28.84 | 0.02565 | 28.77 | 28.8 | 0.02562
10 | 36 | 30 | 0.01622 | 4 | 3 | 8 | 1 | 2 | 28.55 | 29.7 | 0.02559 | 28.56 | 29.7 | 0.02554
11 | 50 | 35 | 0.02171 | 4 | 3 | 8 | 1 | 2 | 34.97 | 36.86 | 0.0397 | 35.02 | 36.87 | 0.03951
12 | 21 | 21 | 0.00941 | 4 | 3 | 8 | 1 | 2 | 18.5 | 19.16 | 0.01325 | 18.49 | 19.16 | 0.01325
13 | 21 | 21 | 0.00941 | 4 | 3 | 8 | 1 | 3 | 18.25 | 18.97 | 0.01363 | 18.25 | 18.97 | 0.01362
14 | 21 | 21 | 0.00941 | 4 | 3 | 8 | 1 | 1 | 19.06 | 19.75 | 0.01231 | 19.06 | 19.75 | 0.0123
15 | 36 | 30 | 0.01622 | 4 | 12 | 8 | 1 | 2 | 33.11 | 32.05 | 0.02972 | 33.11 | 32.04 | 0.02969
16 | 36 | 30 | 0.01622 | 4 | 3 | 8 | 1.1 | 2 | 28.43 | 29.63 | 0.02576 | 28.45 | 29.63 | 0.02571

## Shi2023
Paper information
Authors | Shi et al.
Title | A novel indirect evaporative cooler with porous media under dual spraying modes: A comparative analysis from energy, exergy, and environmental perspectives
Year | 2023
Data type | Numerical data, extracted from graphs
Description | Numerical model validated based on the work of De Antonellis et al. (2019). Investigation of the effect of two water spraying techniques on the IEC performance. Contrary to De Antonellis et al., who focused on the effect of the secondary air conditions on the primary air outlet temperature, Shi et al. considered variable conditions for the primary air inlet temperature.
HEX characteristics |  |  | Configuration
HEX type | IEC |  | pd | wf | pd | sw | sw | wf
Water injection type | Wet surface |  | crossflow |  | crossflow |  | counterflow
Water recirculation | No
Wall material | Stainless steel with porous material layer
Configuration | XPC
Geometry
Length | 0.4 | m
Width | NA | m
Height | NA | m
Channel height | 2-2.5 | m
Wall thickness | NA | m
Number of channels | NA | -
Operating conditions |  |  |  | Test
Primary fluid velocity | 1.5-3.5 | m/s |  | P | Periodic spraying: spray 120s then stop until T_pdo rises by 0.5 K
Secondary fluid velocity | 1-3 | m/s |  | C | Continuous spraying
Secondary-to-Primary flow rate ratio | 0.33-1.33 | kg/kg
Water supplied | NA | kg/s
| Testing conditions | [9 empty] | Inlet conditions | [7 empty] | Outlet conditions
Run | Test | L | h_ch | W | WWR | SPR | Re | Nu | h_T_pd | h_T_sw | T_pdi | w_pdi | v_pdi | T_swi | w_swi | v_swi | T_wfi | m_dot_wf | T_pdo | w_pdo | T_swo | w_wso | epsilon_wb | epsilon_dp
1 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1550.6739 | 7.54 | 24.5563 | 24.5563 | 24 | 0.0074499 | 3 | 25 | 0.011949 | 2 | NA | NA | 21.106 | 0.0074499 | NA | NA | 0.33773 | 0.19982
2 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1534.5966 | 7.54 | 24.6635 | 24.6635 | 26 | 0.0084064 | 3 | 25 | 0.011949 | 2 | NA | NA | 22.2325 | 0.0084064 | NA | NA | 0.41731 | 0.25958
3 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1517.3554 | 7.54 | 24.7795 | 24.7795 | 28 | 0.0094704 | 3 | 25 | 0.011949 | 2 | NA | NA | 23.6369 | 0.0094704 | NA | NA | 0.45995 | 0.29739
4 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1499.8208 | 7.54 | 24.8979 | 24.8979 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.1342 | 0.010652 | NA | NA | 0.48941 | 0.32686
5 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1482.0127 | 7.54 | 25.0184 | 25.0184 | 32 | 0.011964 | 3 | 25 | 0.011949 | 2 | NA | NA | 26.7214 | 0.011964 | NA | NA | 0.50775 | 0.34798
6 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1464.3709 | 7.54 | 25.1375 | 25.1375 | 34 | 0.013417 | 3 | 25 | 0.011949 | 2 | NA | NA | 28.2967 | 0.013417 | NA | NA | 0.52584 | 0.36733
7 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1446.7021 | 7.54 | 25.2563 | 25.2563 | 36 | 0.015025 | 3 | 25 | 0.011949 | 2 | NA | NA | 29.9016 | 0.015025 | NA | NA | 0.54005 | 0.3874
8 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1548.9421 | 7.54 | 24.5693 | 24.5693 | 24 | 0.0074499 | 3 | 25 | 0.011949 | 2 | NA | NA | 21.478 | 0.0074499 | NA | NA | 0.29432 | 0.17226
9 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1533.4108 | 7.54 | 24.6725 | 24.6725 | 26 | 0.0084064 | 3 | 25 | 0.011949 | 2 | NA | NA | 22.4914 | 0.0084064 | NA | NA | 0.38863 | 0.23909
10 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1516.3632 | 7.54 | 24.7871 | 24.7871 | 28 | 0.0094704 | 3 | 25 | 0.011949 | 2 | NA | NA | 23.8575 | 0.0094704 | NA | NA | 0.43669 | 0.27711
11 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1498.9815 | 7.54 | 24.9045 | 24.9045 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.3243 | 0.010652 | NA | NA | 0.47028 | 0.31352
12 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1481.3495 | 7.54 | 25.0237 | 25.0237 | 32 | 0.011964 | 3 | 25 | 0.011949 | 2 | NA | NA | 26.8746 | 0.011964 | NA | NA | 0.49302 | 0.33485
13 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1463.7279 | 7.54 | 25.1426 | 25.1426 | 34 | 0.013417 | 3 | 25 | 0.011949 | 2 | NA | NA | 28.448 | 0.013417 | NA | NA | 0.51189 | 0.36089
14 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1446.0456 | 7.54 | 25.2617 | 25.2617 | 36 | 0.015025 | 3 | 25 | 0.011949 | 2 | NA | NA | 30.0592 | 0.015025 | NA | NA | 0.5261 | 0.3747
15 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1935.4182 | 7.54 | 19.659 | 19.659 | 24 | 0.0074499 | 3 | 25 | 0.011949 | 2 | NA | NA | 21.6086 | 0.0074499 | NA | NA | 0.27907 | 0.16537
16 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1914.7233 | 7.54 | 19.7478 | 19.7478 | 26 | 0.0084064 | 3 | 25 | 0.011949 | 2 | NA | NA | 22.8484 | 0.0084064 | NA | NA | 0.3491 | 0.21859
17 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1893.0049 | 7.54 | 19.8417 | 19.8417 | 28 | 0.0094704 | 3 | 25 | 0.011949 | 2 | NA | NA | 24.2938 | 0.0094704 | NA | NA | 0.3907 | 0.25007
18 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1870.571 | 7.54 | 19.9393 | 19.9393 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.8972 | 0.010652 | NA | NA | 0.41266 | 0.2735
19 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1848.1448 | 7.54 | 20.0369 | 20.0369 | 32 | 0.011964 | 3 | 25 | 0.011949 | 2 | NA | NA | 27.53 | 0.011964 | NA | NA | 0.42997 | 0.29546
20 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1825.9609 | 7.54 | 20.1331 | 20.1331 | 34 | 0.013417 | 3 | 25 | 0.011949 | 2 | NA | NA | 29.1459 | 0.013417 | NA | NA | 0.44755 | 0.31578
21 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1803.5838 | 7.54 | 20.2301 | 20.2301 | 36 | 0.015025 | 3 | 25 | 0.011949 | 2 | NA | NA | 30.8237 | 0.015025 | NA | NA | 0.4584 | 0.33024
22 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1933.4128 | 7.54 | 19.6686 | 19.6686 | 24 | 0.0074499 | 3 | 25 | 0.011949 | 2 | NA | NA | 21.954 | 0.0074499 | NA | NA | 0.23876 | 0.13781
23 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1913.2986 | 7.54 | 19.7548 | 19.7548 | 26 | 0.0084064 | 3 | 25 | 0.011949 | 2 | NA | NA | 23.098 | 0.0084064 | NA | NA | 0.32145 | 0.1981
24 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1891.7136 | 7.54 | 19.8481 | 19.8481 | 28 | 0.0094704 | 3 | 25 | 0.011949 | 2 | NA | NA | 24.5242 | 0.0094704 | NA | NA | 0.36641 | 0.23656
25 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1869.6386 | 7.54 | 19.944 | 19.944 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 26.0667 | 0.010652 | NA | NA | 0.39561 | 0.26015
26 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1847.319 | 7.54 | 20.0411 | 20.0411 | 32 | 0.011964 | 3 | 25 | 0.011949 | 2 | NA | NA | 27.6831 | 0.011964 | NA | NA | 0.41525 | 0.28232
27 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1825.1159 | 7.54 | 20.1375 | 20.1375 | 34 | 0.013417 | 3 | 25 | 0.011949 | 2 | NA | NA | 29.3056 | 0.013417 | NA | NA | 0.43282 | 0.30289
28 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1802.7515 | 7.54 | 20.2344 | 20.2344 | 36 | 0.015025 | 3 | 25 | 0.011949 | 2 | NA | NA | 30.9842 | 0.015025 | NA | NA | 0.44419 | 0.31754
29 | C | 0.4 | 0.004 | NA | 1 | 1.3333 | 753.662 | 7.54 | 24.8397 | 24.8397 | 30 | 0.010652 | 1.5 | 25 | 0.011949 | 2 | NA | NA | 23.4423 | 0.010652 | NA | NA | 0.65958 | 0.44026
30 | C | 0.4 | 0.004 | NA | 1 | 1 | 1002.7965 | 7.54 | 24.864 | 24.864 | 30 | 0.010652 | 2 | 25 | 0.011949 | 2 | NA | NA | 24.1462 | 0.010652 | NA | NA | 0.58877 | 0.39357
31 | C | 0.4 | 0.004 | NA | 1 | 0.8 | 1251.4674 | 7.54 | 24.8828 | 24.8828 | 30 | 0.010652 | 2.5 | 25 | 0.011949 | 2 | NA | NA | 24.6954 | 0.010652 | NA | NA | 0.53354 | 0.35354
32 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1499.8183 | 7.54 | 24.8979 | 24.8979 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.1347 | 0.010652 | NA | NA | 0.48935 | 0.32686
33 | C | 0.4 | 0.004 | NA | 1 | 0.57143 | 1747.9244 | 7.54 | 24.9104 | 24.9104 | 30 | 0.010652 | 3.5 | 25 | 0.011949 | 2 | NA | NA | 25.4967 | 0.010652 | NA | NA | 0.45294 | 0.30018
34 | P | 0.4 | 0.004 | NA | 1 | 1.3333 | 753.1732 | 7.54 | 24.8473 | 24.8473 | 30 | 0.010652 | 1.5 | 25 | 0.011949 | 2 | NA | NA | 23.6619 | 0.010652 | NA | NA | 0.63748 | 0.42025
35 | P | 0.4 | 0.004 | NA | 1 | 1 | 1002.2871 | 7.54 | 24.8699 | 24.8699 | 30 | 0.010652 | 2 | 25 | 0.011949 | 2 | NA | NA | 24.3185 | 0.010652 | NA | NA | 0.57145 | 0.38023
36 | P | 0.4 | 0.004 | NA | 1 | 0.8 | 1250.7955 | 7.54 | 24.8891 | 24.8891 | 30 | 0.010652 | 2.5 | 25 | 0.011949 | 2 | NA | NA | 24.8776 | 0.010652 | NA | NA | 0.51521 | 0.3402
37 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1498.9917 | 7.54 | 24.9044 | 24.9044 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.322 | 0.010652 | NA | NA | 0.47052 | 0.31352
38 | P | 0.4 | 0.004 | NA | 1 | 0.57143 | 1746.9233 | 7.54 | 24.9171 | 24.9171 | 30 | 0.010652 | 3.5 | 25 | 0.011949 | 2 | NA | NA | 25.6914 | 0.010652 | NA | NA | 0.43336 | 0.28684
39 | C | 0.4 | 0.005 | NA | 1 | 1.3333 | 939.7618 | 7.54 | 19.8947 | 19.8947 | 30 | 0.010652 | 1.5 | 25 | 0.011949 | 2 | NA | NA | 24.276 | 0.010652 | NA | NA | 0.57572 | 0.38023
40 | C | 0.4 | 0.005 | NA | 1 | 1 | 1250.4368 | 7.54 | 19.914 | 19.914 | 30 | 0.010652 | 2 | 25 | 0.011949 | 2 | NA | NA | 24.975 | 0.010652 | NA | NA | 0.50542 | 0.33353
41 | C | 0.4 | 0.005 | NA | 1 | 0.8 | 1560.6697 | 7.54 | 19.9282 | 19.9282 | 30 | 0.010652 | 2.5 | 25 | 0.011949 | 2 | NA | NA | 25.4917 | 0.010652 | NA | NA | 0.45344 | 0.30018
42 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1870.5632 | 7.54 | 19.9393 | 19.9393 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.8986 | 0.010652 | NA | NA | 0.41252 | 0.2735
43 | C | 0.4 | 0.005 | NA | 1 | 0.57143 | 2180.3226 | 7.54 | 19.9479 | 19.9479 | 30 | 0.010652 | 3.5 | 25 | 0.011949 | 2 | NA | NA | 26.2106 | 0.010652 | NA | NA | 0.38113 | 0.25348
44 | P | 0.4 | 0.005 | NA | 1 | 1.3333 | 939.2846 | 7.54 | 19.8995 | 19.8995 | 30 | 0.010652 | 1.5 | 25 | 0.011949 | 2 | NA | NA | 24.4483 | 0.010652 | NA | NA | 0.55839 | 0.37355
45 | P | 0.4 | 0.005 | NA | 1 | 1 | 1249.7842 | 7.54 | 19.9188 | 19.9188 | 30 | 0.010652 | 2 | 25 | 0.011949 | 2 | NA | NA | 25.1522 | 0.010652 | NA | NA | 0.48759 | 0.32019
46 | P | 0.4 | 0.005 | NA | 1 | 0.8 | 1559.856 | 7.54 | 19.933 | 19.933 | 30 | 0.010652 | 2.5 | 25 | 0.011949 | 2 | NA | NA | 25.669 | 0.010652 | NA | NA | 0.43562 | 0.28684
47 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1869.6572 | 7.54 | 19.9439 | 19.9439 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 26.0634 | 0.010652 | NA | NA | 0.39595 | 0.26015
48 | P | 0.4 | 0.005 | NA | 1 | 0.57143 | 2179.1713 | 7.54 | 19.9529 | 19.9529 | 30 | 0.010652 | 3.5 | 25 | 0.011949 | 2 | NA | NA | 26.3904 | 0.010652 | NA | NA | 0.36306 | 0.24014
49 | C | 0.4 | 0.004 | NA | 1 | 0.33333 | 1496.9529 | 7.54 | 24.9203 | 24.9203 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1 | NA | NA | 25.7845 | 0.010652 | NA | NA | 0.424 | 0.28017
50 | C | 0.4 | 0.004 | NA | 1 | 0.5 | 1498.6552 | 7.54 | 24.907 | 24.907 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1.5 | NA | NA | 25.3982 | 0.010652 | NA | NA | 0.46284 | 0.30685
51 | C | 0.4 | 0.004 | NA | 1 | 0.66667 | 1499.8209 | 7.54 | 24.8979 | 24.8979 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.1342 | 0.010652 | NA | NA | 0.48941 | 0.32686
52 | C | 0.4 | 0.004 | NA | 1 | 0.83333 | 1500.5155 | 7.54 | 24.8925 | 24.8925 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2.5 | NA | NA | 24.977 | 0.010652 | NA | NA | 0.50522 | 0.33353
53 | C | 0.4 | 0.004 | NA | 1 | 1 | 1500.9773 | 7.54 | 24.8889 | 24.8889 | 30 | 0.010652 | 3 | 25 | 0.011949 | 3 | NA | NA | 24.8725 | 0.010652 | NA | NA | 0.51572 | 0.3402
54 | P | 0.4 | 0.004 | NA | 1 | 0.33333 | 1496.2625 | 7.54 | 24.9257 | 24.9257 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1 | NA | NA | 25.9413 | 0.010652 | NA | NA | 0.40822 | 0.2735
55 | P | 0.4 | 0.004 | NA | 1 | 0.5 | 1497.9696 | 7.54 | 24.9123 | 24.9123 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1.5 | NA | NA | 25.5537 | 0.010652 | NA | NA | 0.44721 | 0.29351
56 | P | 0.4 | 0.004 | NA | 1 | 0.66667 | 1499.0058 | 7.54 | 24.9043 | 24.9043 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.3188 | 0.010652 | NA | NA | 0.47084 | 0.31352
57 | P | 0.4 | 0.004 | NA | 1 | 0.83333 | 1499.7488 | 7.54 | 24.8985 | 24.8985 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2.5 | NA | NA | 25.1505 | 0.010652 | NA | NA | 0.48777 | 0.32019
58 | P | 0.4 | 0.004 | NA | 1 | 1 | 1500.1735 | 7.54 | 24.8952 | 24.8952 | 30 | 0.010652 | 3 | 25 | 0.011949 | 3 | NA | NA | 25.0543 | 0.010652 | NA | NA | 0.49743 | 0.32686
59 | C | 0.4 | 0.005 | NA | 1 | 0.33333 | 1868.0172 | 7.54 | 19.9521 | 19.9521 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1 | NA | NA | 26.3619 | 0.010652 | NA | NA | 0.36592 | 0.24014
60 | C | 0.4 | 0.005 | NA | 1 | 0.5 | 1869.7271 | 7.54 | 19.9435 | 19.9435 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1.5 | NA | NA | 26.0507 | 0.010652 | NA | NA | 0.39723 | 0.26015
61 | C | 0.4 | 0.005 | NA | 1 | 0.66667 | 1870.5686 | 7.54 | 19.9393 | 19.9393 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 25.8976 | 0.010652 | NA | NA | 0.41262 | 0.2735
62 | C | 0.4 | 0.005 | NA | 1 | 0.83333 | 1871.1205 | 7.54 | 19.9366 | 19.9366 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2.5 | NA | NA | 25.7973 | 0.010652 | NA | NA | 0.42271 | 0.28017
63 | C | 0.4 | 0.005 | NA | 1 | 1 | 1871.6038 | 7.54 | 19.9342 | 19.9342 | 30 | 0.010652 | 3 | 25 | 0.011949 | 3 | NA | NA | 25.7095 | 0.010652 | NA | NA | 0.43154 | 0.28684
64 | P | 0.4 | 0.005 | NA | 1 | 0.33333 | 1867.1489 | 7.54 | 19.9564 | 19.9564 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1 | NA | NA | 26.5202 | 0.010652 | NA | NA | 0.35 | 0.23347
65 | P | 0.4 | 0.005 | NA | 1 | 0.5 | 1868.7203 | 7.54 | 19.9486 | 19.9486 | 30 | 0.010652 | 3 | 25 | 0.011949 | 1.5 | NA | NA | 26.2339 | 0.010652 | NA | NA | 0.3788 | 0.25348
66 | P | 0.4 | 0.005 | NA | 1 | 0.66667 | 1869.6527 | 7.54 | 19.9439 | 19.9439 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2 | NA | NA | 26.0642 | 0.010652 | NA | NA | 0.39586 | 0.26015
67 | P | 0.4 | 0.005 | NA | 1 | 0.83333 | 1870.1659 | 7.54 | 19.9413 | 19.9413 | 30 | 0.010652 | 3 | 25 | 0.011949 | 2.5 | NA | NA | 25.9708 | 0.010652 | NA | NA | 0.40525 | 0.26682
68 | P | 0.4 | 0.005 | NA | 1 | 1 | 1870.6488 | 7.54 | 19.9389 | 19.9389 | 30 | 0.010652 | 3 | 25 | 0.011949 | 3 | NA | NA | 25.883 | 0.010652 | NA | NA | 0.41408 | 0.2735